## Summary
PUMPGURU — Pump Protection Report
Period: Last 7 day(s) (2026-08-20T17:37:45 to now)
Generated: 2026-08-27 17:37:45
Metric | Value
Total data points logged | 3313
Snapshots with an active fault | 505
Estimated uptime (fault-free) % | 84.76%
Total fault events (ACTIVE transitions) | 41
Fault Frequency Breakdown
Fault Type | Times Triggered
dry_run | 20
undervoltage | 10
overvoltage | 4
overload | 3
stall_pump | 2
phase_loss | 2
Measurement Analysis
Parameter | Min | Max | Average | Unit
Current B Phase | 0 | 49.9 | 8.65 | A
Current R Phase | 0 | 49.9 | 9.38 | A
Current Y Phase | 0 | 48 | 6.35 | A
Voltage B-R | 0 | 535 | 290.53 | V
Voltage R-Y | 0 | 533 | 295.16 | V
Voltage Y-B | 0 | 535 | 280.39 | V
Recent Run Minutes (Pump 1) | 0 | 99.67 | 2.36 | min
Recent Run Minutes (Pump 2) | 0 | 98.73 | 8.91 | min
Total Run Minutes (Pump 1) | 0 | 586.1 | 15.61 | min
Total Run Minutes (Pump 2) | 0 | 596.1 | 65.96 | min
Set ON Time | 0 | 89.64 | 13.66 | M
Set OFF Time | 0 | 94.71 | 3.07 | M
Set Current 1 | 4.6 | 180 | 20.79 | A
Set Current 2 | 1.8 | 180 | 26.51 | A
Set Dry-Run Current | 0 | 400 | 49.13 | %
Bottom Tank Low Sensor | 0 | 1 | 0.93
Bottom Tank High Sensor | 0 | 250 | 4.4
Top Tank Low Sensor | 0 | 184 | 0.68
Top Tank High Sensor | 0 | 102 | 1.45
Auto/Manual Mode | 51 | 102 | 74.3
Pump Run/Stop Control | 0 | 1 | 0.33
Pump Selection Mode | 0 | 1 | 0.83
Phase Balance Analysis
Voltage Imbalance (avg, max-min / mean) | 5.12%
Current Imbalance (avg, max-min / mean) | 212.47%

## Trends
Timestamp | Current B Phase | Current R Phase | Current Y Phase | Voltage B-R | Voltage R-Y | Voltage Y-B | Recent Run Minutes (Pump 1) | Recent Run Minutes (Pump 2) | Total Run Minutes (Pump 1) | Total Run Minutes (Pump 2) | Set ON Time | Set OFF Time | Set Current 1 | Set Current 2 | Set Dry-Run Current | Bottom Tank Low Sensor | Bottom Tank High Sensor | Top Tank Low Sensor | Top Tank High Sensor | Auto/Manual Mode | Pump Run/Stop Control | Pump Selection Mode
2026-08-25T14:24:47 | 34 | 27 |  |  |  | 44
2026-08-25T14:24:52 | 34 | 27.2 |  |  |  | 44
2026-08-25T14:24:58 | 34 | 26.9 |  |  |  | 44
2026-08-25T14:25:04 | 34 | 26.8 |  |  |  | 44
2026-08-25T14:25:10 | 34 | 26.8 |  |  |  | 44
2026-08-25T14:25:15 | 34 | 27.5 |  |  |  | 44
2026-08-25T14:25:20 | 34 | 13.2 |  |  |  | 44
2026-08-25T14:25:26 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:31 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:36 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:42 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:47 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:53 | 34 | 6.7 |  |  |  | 44
2026-08-25T14:25:59 | 34 | 6.8 |  |  |  | 43.8
2026-08-25T14:26:04 | 34 | 6.7 |  |  |  | 43.7
2026-08-25T14:26:10 | 34 | 6.7 |  |  |  | 43.7
2026-08-25T14:26:15 | 34 | 6.7 |  |  |  | 43.7
2026-08-25T14:26:21 | 34 | 6.7 |  |  |  | 43.7
2026-08-25T14:26:26 | 34 | 6.7 |  |  |  | 43.7
2026-08-25T14:26:31 | 34 | 6.8 |  |  |  | 43.9
2026-08-25T14:26:37 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:26:42 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:26:47 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:26:54 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:26:59 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:05 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:10 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:15 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:21 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:26 | 34 | 6.8 |  |  |  | 44
2026-08-25T14:27:32 | 34 | 6.8 |  |  |  | 43.9
2026-08-25T14:27:37 | 34 | 6.8 |  |  |  | 44.1
2026-08-25T14:27:42 | 34 | 6.9 |  |  |  | 44.1
2026-08-25T14:27:49
2026-08-25T14:27:54
2026-08-25T14:27:59
2026-08-25T14:28:04
2026-08-25T14:28:09
2026-08-25T14:28:14
2026-08-25T14:28:19
2026-08-25T14:28:24
2026-08-25T14:28:29
2026-08-25T14:28:34
2026-08-25T14:28:39
2026-08-25T14:28:44
2026-08-25T14:28:49
2026-08-25T14:28:54
2026-08-25T14:28:59
2026-08-25T14:29:04
2026-08-25T14:29:09
2026-08-25T14:29:14
2026-08-25T14:29:19
2026-08-25T14:29:24
2026-08-25T14:29:29
2026-08-25T14:29:34
2026-08-25T14:29:39
2026-08-25T14:29:44
2026-08-25T14:29:49
2026-08-25T14:29:54
2026-08-25T14:29:59
2026-08-25T14:30:04
2026-08-25T14:30:09
2026-08-25T14:30:14
2026-08-25T14:30:19
2026-08-25T14:30:24
2026-08-25T14:30:29
2026-08-25T14:30:34
2026-08-25T14:30:39
2026-08-25T14:30:44
2026-08-25T14:30:49
2026-08-25T14:30:54
2026-08-25T14:30:59
2026-08-25T14:31:04
2026-08-25T14:31:10
2026-08-25T14:32:29
2026-08-25T14:32:35
2026-08-25T14:32:40
2026-08-25T14:32:45
2026-08-25T14:32:50
2026-08-25T14:32:55
2026-08-25T14:33:00
2026-08-25T14:33:05
2026-08-25T14:33:10
2026-08-25T14:33:15
2026-08-25T14:33:20
2026-08-25T14:33:25
2026-08-25T14:33:30
2026-08-25T14:33:35
2026-08-25T14:33:40
2026-08-25T14:33:45
2026-08-25T14:33:50
2026-08-25T14:33:55
2026-08-25T14:34:00
2026-08-25T14:34:05
2026-08-25T14:34:10
2026-08-25T14:34:15
2026-08-25T14:34:20
2026-08-25T14:34:25
2026-08-25T14:34:30
2026-08-25T14:34:35
2026-08-25T14:34:40
2026-08-25T14:34:45
2026-08-25T14:34:50
2026-08-25T14:34:55
2026-08-25T14:35:00
2026-08-25T14:35:05
2026-08-25T15:13:30 | 34 | 0 |  |  |  | 0
2026-08-25T15:13:35 | 34 | 0 |  |  |  | 0
2026-08-25T15:13:41 | 34 | 0 |  |  |  | 0
2026-08-25T15:13:46 | 34 | 0 |  |  |  | 0
2026-08-25T15:13:52 | 34 | 0 |  |  |  | 0
2026-08-25T15:13:59 | 34 | 0 |  |  |  | 0
2026-08-25T15:14:04 | 34 | 0 |  |  |  | 0
2026-08-25T15:14:11 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:00 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:05 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:12 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:18 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:24 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:30 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:35 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:41 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:47 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:53 | 34 | 0 |  |  |  | 0
2026-08-25T15:15:59 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:06 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:11 | 34 | 0 | 0 |  |  | 0
2026-08-25T15:16:18 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:23 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:29 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:35 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:40 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:46 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:52 | 34 | 0 |  |  |  | 0
2026-08-25T15:16:57 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:03 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:08 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:14 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:20 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:26 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:32 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:39 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:44 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:51 | 34 | 0 |  |  |  | 0
2026-08-25T15:17:56 | 34 | 0 |  |  |  | 0
2026-08-25T15:18:03 | 34 | 0 |  |  |  | 0
2026-08-25T15:18:09 | 34 | 0 |  |  |  | 0
2026-08-25T15:18:15 | 34 | 0 |  |  |  | 0
2026-08-25T15:18:21
2026-08-25T15:18:26
2026-08-25T15:18:32
2026-08-25T15:18:37
2026-08-25T15:18:42
2026-08-25T15:18:48
2026-08-25T15:18:53
2026-08-25T15:18:58
2026-08-25T15:19:04
2026-08-25T15:19:09
2026-08-25T15:19:14
2026-08-25T15:19:20
2026-08-25T15:19:25
2026-08-25T15:19:30
2026-08-25T15:19:36
2026-08-25T15:19:41
2026-08-25T15:19:46
2026-08-25T15:19:52
2026-08-25T15:19:57
2026-08-25T15:20:02
2026-08-25T15:20:08
2026-08-25T15:20:13
2026-08-25T15:20:18
2026-08-25T15:20:24
2026-08-25T15:20:29
2026-08-25T15:20:34
2026-08-25T15:20:40
2026-08-25T15:20:58 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:04 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:15 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:21 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:26 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:32 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:38 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:43 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:49 | 34 | 0 |  |  |  | 0
2026-08-25T15:21:54 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:00 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:07 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:12 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:19 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:25 | 34 | 0 |  | 0 |  | 0
2026-08-25T15:22:30 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:36 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:47 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:52 | 34 | 0 |  |  |  | 0
2026-08-25T15:22:58 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:04 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:09 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:15 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:20 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:26 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:32 | 34 | 0 |  | 0 |  | 0
2026-08-25T15:23:37 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:43 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:49 | 34 | 0 |  |  |  | 0
2026-08-25T15:23:55 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:01 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:07 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:13 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:19 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:25 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:37 | 34 | 0 |  |  |  | 0
2026-08-25T15:24:42 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:24:48 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:24:53 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:24:59 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:25:05 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:25:10 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:25:16 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:25:22 | 34 | 7.4 |  | 0 |  | 44
2026-08-25T15:25:27 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:25:33 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:25:38 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:25:45 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:25:51 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:02 | 34 | 7.5 |  |  |  | 44
2026-08-25T15:26:08 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:13 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:19 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:24 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:30 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:36 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:41 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:47 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:53 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:26:58 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:27:09 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:27:15 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:27:20 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:27:26 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:27:32 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:33:53 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:33:58 | 34 | 7.4 |  |  |  | 43.9
2026-08-25T15:34:05 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:34:16 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:34:22 | 34 | 7.4 |  |  |  | 44
2026-08-25T15:45:44
2026-08-25T15:45:50
2026-08-25T15:45:56
2026-08-25T15:46:02
2026-08-25T15:46:08
2026-08-25T15:46:14
2026-08-25T15:46:20
2026-08-25T15:46:25
2026-08-25T15:48:44
2026-08-25T15:48:51
2026-08-25T15:48:58
2026-08-25T15:49:04
2026-08-25T15:49:10
2026-08-25T15:49:16
2026-08-25T15:49:21
2026-08-25T15:49:28
2026-08-25T15:49:34
2026-08-25T15:49:40
2026-08-25T15:49:46
2026-08-25T15:49:52
2026-08-25T15:49:59
2026-08-25T15:50:05
2026-08-25T15:50:10
2026-08-25T15:50:16
2026-08-25T15:50:23
2026-08-25T15:50:29
2026-08-25T15:50:35
2026-08-25T15:50:41
2026-08-25T15:50:47
2026-08-25T15:50:53
2026-08-25T15:50:59
2026-08-25T15:51:05
2026-08-25T15:51:12
2026-08-25T15:51:18
2026-08-25T15:51:24
2026-08-25T15:51:30
2026-08-25T15:51:36
2026-08-25T15:51:42
2026-08-25T15:51:49
2026-08-25T15:51:54
2026-08-25T15:55:29 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:55:34 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:55:40 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:55:45 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:55:50 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:55:55 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:00 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:05 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:10 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:15 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:20 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:25 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:31 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:36 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:41 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:46 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:51 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:56:56 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:01 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:06 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:11 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:16 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:22 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:27 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:32 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:37 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:42 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:57:47
2026-08-25T15:57:52
2026-08-25T15:57:58
2026-08-25T15:58:03
2026-08-25T15:58:08
2026-08-25T15:58:14
2026-08-25T15:58:19
2026-08-25T15:58:24
2026-08-25T15:58:30
2026-08-25T15:58:35
2026-08-25T15:58:40
2026-08-25T15:58:46
2026-08-25T15:58:51
2026-08-25T15:58:56
2026-08-25T15:59:03 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:08 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:13 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:18 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:24 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:29 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:34 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:39 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:44 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:49 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:54 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T15:59:59 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:04 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:10 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:15 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:20 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:25 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:30 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:35 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:40 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:45 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:50 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:00:55 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:01 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:06 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:11 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:16 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:21 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:26 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:31 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:36 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:41 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:46 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:52 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:01:57 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:02 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:07 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:12 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:17 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:22 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:27 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:32 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:38 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:43 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:48 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:53 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:02:58 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:03 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:08 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:13 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:18 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:23 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:29 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:34 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:39 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:03:44 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:28 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:33 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:38 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:43 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:48 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:54 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:07:59 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:08:04 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:08:09 | 0.4 | 34 | 48 | 0 | 0 | 0
2026-08-25T16:08:15 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:08:20 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:08:25
2026-08-25T16:08:31
2026-08-25T16:08:36
2026-08-25T16:08:41
2026-08-25T16:08:47
2026-08-25T16:08:52
2026-08-25T16:08:57
2026-08-25T16:09:03
2026-08-25T16:09:08
2026-08-25T16:09:14 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:19 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:24 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:29 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:34 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:40 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:46 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:53 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:09:59 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:05 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:10 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:15 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:20 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:25 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:30 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:35 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:40 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:46 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:51 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:10:56 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:01 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:06 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:11 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:16 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:21 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:26 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:31 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:36 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:42 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:47 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:52 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:11:57 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:02 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:07 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:12 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:17 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:22 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:27 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:33 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:38 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:43 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:48 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:53 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:12:58 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:03 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:08 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:13 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:18 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:23 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:29 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:34 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:40 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:45 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:50 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:13:55 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:00 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:05 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:10 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:15 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:21 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:26 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:31 | 0.4 | 34 | 12 | 0 | 0 | 0
2026-08-25T16:14:36
2026-08-25T16:14:41
2026-08-25T16:14:47
2026-08-25T16:14:52
2026-08-25T16:14:57
2026-08-25T16:15:03
2026-08-25T16:15:08
2026-08-25T16:15:13
2026-08-25T16:15:19
2026-08-25T16:15:24
2026-08-25T16:15:29
2026-08-25T16:15:35
2026-08-25T16:15:40
2026-08-25T16:15:45
2026-08-25T16:15:51
2026-08-25T16:15:56
2026-08-25T16:16:01
2026-08-25T16:16:07
2026-08-25T16:16:12
2026-08-25T16:16:17 | 1.2 | 34 | 12 | 5.5 | 42 | 44.3
2026-08-25T16:16:22 | 0 | 34 | 12 | 5.5 | 42.1 | 44.3
2026-08-25T16:16:27 | 1.2 | 34 | 12 | 5.5 | 42.1 | 44.4
2026-08-25T16:16:33 | 1.2 | 34 | 12 | 5.5 | 42.1 | 44.4
2026-08-25T16:16:38 | 0 | 34 | 12 | 5.6 | 42.2 | 44.5
2026-08-25T16:16:43 | 1.2 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:16:49 | 1.2 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:16:54 | 0 | 34 | 12 | 5.5 | 42.1 | 44.4
2026-08-25T16:16:59 | 0 | 34 | 12 | 5.5 | 42.1 | 44.3
2026-08-25T16:17:04 | 0 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:17:09 | 0 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:17:14 | 1.2 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:17:19 | 1.2 | 34 | 12 | 5.5 | 42.2 | 44.3
2026-08-25T16:17:25 | 1.2 | 34 | 12 | 5.5 | 42.2 | 44.3
2026-08-25T16:17:30 | 0 | 34 | 12 | 5.5 | 42.2 | 44.3
2026-08-25T16:17:35 | 0 | 34 | 12 | 5.5 | 42.2 | 44.4
2026-08-25T16:17:40 | 1.2 | 34 | 12 | 8 | 42.1 | 44.3
2026-08-25T16:17:45 | 0 | 34 | 12 | 9.1 | 42.1 | 44.2
2026-08-25T16:17:50 | 0 | 34 | 12 | 9.1 | 42.1 | 44.2
2026-08-25T16:17:55 | 1.2 | 34 | 12 | 9.1 | 42.2 | 44.3
2026-08-25T16:18:00 | 0 | 34 | 12 | 9.1 | 42.2 | 44.4
2026-08-25T16:18:05 | 0 | 34 | 12 | 9.1 | 42.2 | 44.4
2026-08-25T16:18:10 | 0 | 34 | 12 | 9.1 | 42.1 | 44.4
2026-08-25T16:18:15 | 1.2 | 34 | 12 | 9.1 | 42.2 | 44.3
2026-08-25T16:18:21 | 1.2 | 34 | 12 | 9 | 42.2 | 44.3
2026-08-25T16:18:26 | 0 | 34 | 12 | 9 | 42.2 | 44.3
2026-08-25T16:18:31 | 1.2 | 34 | 12 | 9 | 42.2 | 44.3
2026-08-25T16:18:36 | 0 | 34 | 12 | 9 | 42.1 | 44.3
2026-08-25T16:19:19
2026-08-25T16:20:17 | 0.1 | 49.9 | 0.1 | 0
2026-08-25T16:20:50
2026-08-25T16:20:55
2026-08-25T16:21:01
2026-08-25T16:21:06
2026-08-25T16:21:11
2026-08-25T16:21:17
2026-08-25T16:21:22
2026-08-25T16:21:27
2026-08-25T16:21:33
2026-08-25T16:21:38
2026-08-25T16:21:43
2026-08-25T16:21:48
2026-08-25T16:21:54
2026-08-25T16:21:59
2026-08-25T16:22:04
2026-08-25T16:22:10
2026-08-25T16:22:15
2026-08-25T16:22:20
2026-08-25T16:22:26
2026-08-25T16:22:31
2026-08-25T16:22:36
2026-08-25T16:25:04 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.6
2026-08-25T16:25:09 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.6
2026-08-25T16:25:15 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:25:20 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:25:25 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:25:30 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.5
2026-08-25T16:25:35 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.5
2026-08-25T16:25:40 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.5
2026-08-25T16:25:45 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:25:50 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:25:55 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:26:00 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:26:05 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:10 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:15 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:20 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.7
2026-08-25T16:26:26 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:31 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:36 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:41 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:26:46 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:26:51 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.6
2026-08-25T16:26:56 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:01 | 0.1 | 49.9 | 0.1 | 7.9 | 45.7 | 45.6
2026-08-25T16:27:06 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:27:11 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:16 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:21 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:26 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:31 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.6
2026-08-25T16:27:37 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:27:42 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:27:47 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:27:52 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:27:57 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:02 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:07 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:12 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:28:17 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:22 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:27 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:28:32 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:28:37 | 0.1 | 49.9 | 0.1 | 7.9 | 46 | 45.9
2026-08-25T16:28:42 | 0.1 | 49.9 | 0.1 | 7.9 | 46 | 45.8
2026-08-25T16:28:47 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:28:53 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:28:58 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:29:03 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:29:08 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:29:13 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:29:18 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:29:23 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:29:28 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.7
2026-08-25T16:29:33 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:29:38 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:29:43 | 0.1 | 49.9 | 0.1 | 7.9 | 45.8 | 45.7
2026-08-25T16:29:48 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:29:53 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.9
2026-08-25T16:29:58 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:30:04 | 0.1 | 49.9 | 0.1 | 7.9 | 45.9 | 45.8
2026-08-25T16:34:07 | 49.9 | 7.8 |  |  |  | 45.2
2026-08-25T16:34:13 | 49.9 | 7.8 |  |  |  | 45.3
2026-08-25T16:34:19 | 49.9 | 7.8 |  |  |  | 45.3
2026-08-25T16:34:24 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:34:30 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:34:36 | 49.9 | 7.8 |  |  |  | 45.3
2026-08-25T16:34:42 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:34:47 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:34:52 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:34:58 | 49.9 | 7.8 |  |  |  | 45.4
2026-08-25T16:35:04 | 49.9 | 7.8 |  |  |  | 45.5
2026-08-25T16:35:09 | 49.9 | 7.8 |  |  |  | 45.5
2026-08-25T16:35:15 | 49.9 | 7.9 |  |  |  | 45.5
2026-08-25T16:35:20 | 49.9 | 7.9 |  |  |  | 45.5
2026-08-25T16:35:25 | 49.9 | 7.9 |  |  |  | 45.7
2026-08-25T16:35:31 | 49.9 | 8 |  |  |  | 46.1
2026-08-25T16:35:36 | 49.9 | 8 |  |  |  | 46.3
2026-08-25T16:35:42 | 49.9 | 8 |  |  |  | 46.2
2026-08-25T16:35:47 | 49.9 | 8 |  |  |  | 46.1
2026-08-25T16:35:53 | 49.9 | 8 |  |  |  | 46.1
2026-08-25T16:35:58 | 49.9 | 8 |  |  |  | 46.1
2026-08-25T16:36:05 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:10 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:16 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:21 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:27 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:36:32 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:38 | 49.9 | 7.9 |  |  |  | 46.1
2026-08-25T16:36:43 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:49 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:36:54 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:37:01 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:37:06 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:37:12 | 49.9 | 7.9 |  |  |  | 46
2026-08-25T16:37:17 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:23 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:28 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:34 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:40 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:46 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:51 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:37:58 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:38:03 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:38:09 | 49.9 | 7.9 |  |  |  | 45.9
2026-08-25T16:38:17 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:22 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:27 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:32 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:38 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:43 | 45.8 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:48 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:53 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:38:58 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:03 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:08 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:13 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:18 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:23 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:28 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:33 | 45.9 | 45.9 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:38 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:43 | 45.9 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:48 | 45.8 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:53 | 45.8 | 45.8 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:39:58 | 45.8 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:04 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:09 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:14 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:19 | 45.8 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:24 | 45.8 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:29 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:34 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:39 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:44 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:49 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:54 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:40:59 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:04 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:09 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:14 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:19 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:24 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:30 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:35 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:40 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:45 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:50 | 45.8 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:41:55 | 45.8 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:00 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:05 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:10 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:15 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:20 | 45.7 | 45.7 | 7.8 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:25 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:30 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:35 | 45.7 | 45.7 | 7.9 | 7.9 | 7.9 | 49.9
2026-08-25T16:42:42 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:42:47 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:42:52 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:42:57 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:02 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:07 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:12 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:17 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:22 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:27 |  |  |  | 7.9 | 7.9 | 49.9
2026-08-25T16:43:31
2026-08-25T16:43:36
2026-08-25T16:43:41
2026-08-25T16:43:46
2026-08-25T16:43:50 |  |  |  |  | 45.6
2026-08-25T16:43:55 |  |  |  |  | 45.6
2026-08-25T16:44:00 |  |  |  |  | 45.6
2026-08-25T16:44:05 |  |  |  |  | 45.6
2026-08-25T16:44:10 |  |  |  |  | 45.6
2026-08-25T16:44:15 |  |  |  |  | 45.7
2026-08-25T16:44:20 |  |  |  |  | 45.6
2026-08-25T16:44:25 |  |  |  |  | 45.6
2026-08-25T16:44:36 |  |  |  |  | 45.7 | 45.8
2026-08-25T16:44:41 |  |  |  |  | 45.7 | 45.8
2026-08-25T16:44:46 |  |  |  |  | 45.7 | 45.8
2026-08-25T16:44:51 |  |  |  |  | 45.7 | 45.8
2026-08-25T16:44:56 |  |  |  |  | 45.7 | 45.8
2026-08-25T16:45:00 |  |  |  | 45.7 | 45.7 | 45.8
2026-08-25T16:45:05 |  |  |  | 45.7 | 45.7 | 45.7
2026-08-25T16:45:10 |  |  |  | 45.7 | 45.7 | 45.8
2026-08-25T16:45:15 |  |  |  | 45.7 | 45.7 | 45.7
2026-08-25T16:45:20 |  |  |  | 45.7 | 45.7 | 45.7
2026-08-25T16:45:25 |  |  |  | 45.7 | 45.7 | 45.7
2026-08-25T16:45:32 |  | 7.9 |  | 45.9 | 45.9 | 45.9
2026-08-25T16:45:37 |  | 7.9 |  | 45.8 | 45.8 | 45.9
2026-08-25T16:45:42 |  | 7.9 |  | 45.8 | 45.9 | 45.9
2026-08-25T16:45:47 |  | 7.9 |  | 45.7 | 45.8 | 45.9
2026-08-25T16:45:52 |  | 7.9 | 7.9 | 45.7 | 45.7 | 45.8
2026-08-25T16:45:57 |  | 7.9 | 7.9 | 45.8 | 45.8 | 45.9
2026-08-25T16:46:02 |  | 7.9 | 7.9 | 45.8 | 45.8 | 45.9
2026-08-25T16:46:07 |  | 7.9 | 7.9 | 45.8 | 45.8 | 45.9
2026-08-25T16:46:13 |  | 7.9 | 7.9 | 45.7 | 45.7 | 45.9
2026-08-25T16:46:17 | 7.9 | 7.9 | 7.9 | 45.7 | 45.8 | 45.8
2026-08-25T16:46:22 | 7.9 | 7.9 | 7.9 | 45.7 | 45.7 | 45.9
2026-08-25T16:46:27 | 7.9 | 7.9 | 7.9 | 45.7 | 45.7 | 45.9
2026-08-25T16:46:33 | 7.9 | 7.9 | 7.9 | 45.7 | 45.7 | 45.9
2026-08-25T16:46:38 | 7.9 | 7.9 | 7.9 | 45.7 | 45.8 | 45.9
2026-08-25T16:46:43 | 7.9 | 7.9 | 7.9 | 45.7 | 45.8 | 45.9
2026-08-25T16:46:48 | 7.9 | 7.9 | 7.9 | 45.7 | 45.7 | 45.9
2026-08-25T16:46:53 | 7.9 | 7.9 | 7.9 | 45.8 | 45.7 | 45.9
2026-08-25T16:46:58 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 45.9
2026-08-25T16:47:03 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:08 | 7.9 | 7.9 | 7.9 | 45.8 | 45.7 | 45.9
2026-08-25T16:47:13 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:18 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:47:23 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:28 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:33 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:38 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:43 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:47:48 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:47:53 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:47:58 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:48:03 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:48:09 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 45.9
2026-08-25T16:48:14 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 45.9
2026-08-25T16:48:19 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:48:24 | 7.9 | 7.9 | 7.9 | 45.8 | 45.8 | 45.9
2026-08-25T16:48:29 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 46
2026-08-25T16:48:34 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:48:39 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:48:44 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:48:49 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 46
2026-08-25T16:48:54 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:48:59 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:49:04 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:49:09 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:49:14 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:49:19 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.2
2026-08-25T16:49:24 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.2
2026-08-25T16:49:29 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.2
2026-08-25T16:49:34 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:49:40 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:49:45 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:49:50 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:49:55 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:50:00 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:50:05 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:50:10 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:15 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:20 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:25 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:30 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:35 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:40 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:45 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46.1
2026-08-25T16:50:50 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:50:55 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:51:00 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:05 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:11 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:16 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:51:21 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:26 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:51:31 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:36 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:41 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:51:46 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:51:51 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:51:56 | 7.9 | 7.9 | 7.9 | 46 | 46 | 46.1
2026-08-25T16:52:01 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:52:06 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:52:11 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:52:16 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 45.9
2026-08-25T16:52:21 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:52:26 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 45.9
2026-08-25T16:52:31 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:52:36 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:52:42 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:52:47 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:52:52 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:52:57 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:53:02 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46.1
2026-08-25T16:53:07 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:53:12 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 46
2026-08-25T16:53:17 | 7.9 | 7.9 | 7.9 | 45.8 | 45.7 | 45.9
2026-08-25T16:53:22 | 7.9 | 7.9 | 7.9 | 45.9 | 45.8 | 46
2026-08-25T16:53:27 | 7.9 | 7.9 | 7.9 | 45.8 | 45.8 | 46
2026-08-25T16:53:32 | 7.9 | 7.9 | 7.9 | 45.8 | 45.8 | 46
2026-08-25T16:53:37 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:53:42 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:53:47 | 7.9 | 7.9 | 7.9 | 46 | 45.9 | 46
2026-08-25T16:53:52 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:53:57 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:54:02 | 7.9 | 7.9 | 7.9 | 45.9 | 45.9 | 46
2026-08-25T16:54:08 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:14 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:20 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:26 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:33 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:38 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:44 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:50 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:54:56 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:02 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:55:08 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:15 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:20 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:27 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:33 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:55:39 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:55:45 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:55:51 | 49.9 | 7.9 |  |  |  | 459
2026-08-25T16:55:57 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:56:04 | 49.9 | 7.9 |  |  |  | 460
2026-08-25T16:56:29 | 7.9 | 7.9 | 7.9 | 460 | 460 | 461
2026-08-25T16:56:35 | 7.9 | 7.9 | 7.9 | 460 | 459 | 461
2026-08-25T16:56:40 | 7.9 | 7.9 | 7.9 | 459 | 459 | 461
2026-08-25T16:56:46 | 7.9 | 7.9 | 7.9 | 460 | 461 | 461
2026-08-25T16:56:51 | 7.9 | 7.9 | 7.9 | 460 | 460 | 461
2026-08-25T16:56:56 | 7.9 | 7.9 | 7.9 | 460 | 460 | 461
2026-08-25T16:57:03 | 7.9 | 7.9 | 7.9 | 460 | 461 | 462
2026-08-25T16:57:09 | 7.9 | 7.9 | 7.9 | 460 | 460 | 462
2026-08-25T16:57:14 | 7.9 | 7.9 | 7.9 | 460 | 459 | 462
2026-08-25T16:57:19 | 7.9 | 7.9 | 7.9 | 459 | 459 | 462
2026-08-25T16:57:24 | 7.9 | 7.9 | 7.9 | 460 | 459 | 462
2026-08-25T16:57:30 | 7.9 | 7.9 | 7.9 | 459 | 459 | 461
2026-08-25T16:57:35 | 7.9 | 7.9 | 7.9 | 459 | 459 | 461
2026-08-25T16:57:40 | 7.9 | 7.9 | 7.9 | 459 | 459 | 461
2026-08-25T16:57:45 | 7.9 | 7.9 | 7.9 | 459 | 459 | 461
2026-08-25T16:57:50 | 7.9 | 7.9 | 7.9 | 460 | 460 | 462
2026-08-25T16:57:56 | 8 | 7.9 | 8 | 461 | 461 | 463
2026-08-25T16:58:01 | 8 | 7.9 | 7.9 | 461 | 461 | 462
2026-08-25T16:58:06 | 8 | 7.9 | 7.9 | 461 | 461 | 462
2026-08-25T16:58:11 | 8 | 7.9 | 7.9 | 461 | 461 | 461
2026-08-25T16:58:16 | 8 | 7.9 | 7.9 | 462 | 461 | 461
2026-08-25T16:58:21 | 7.9 | 7.9 | 7.9 | 497 | 497 | 461
2026-08-25T16:58:29 | 8 | 8 | 8 | 463 | 463 | 463
2026-08-25T16:58:34 | 8 | 8 | 8 | 220 | 219 | 225
2026-08-25T16:58:39 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T17:01:33 | 0 | 0 | 0 | 44.2 | 44.1 | 44.2
2026-08-25T17:01:38 | 0 | 0 | 0 | 44.2 | 44.2 | 44.3
2026-08-25T17:01:43 | 0 | 0 | 0 | 44.2 | 44.1 | 44.4
2026-08-25T17:01:48 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:01:53 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:01:58 | 0 | 0 | 0 | 44.1 | 44 | 44.3
2026-08-25T17:02:03 | 0 | 0 | 0 | 44.1 | 44.1 | 44.2
2026-08-25T17:02:08 | 0 | 0 | 0 | 44.1 | 44 | 44.2
2026-08-25T17:02:13 | 0 | 0 | 0 | 44.1 | 44 | 44.3
2026-08-25T17:02:18 | 0 | 0 | 0 | 44.1 | 44.1 | 44.2
2026-08-25T17:02:23 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:02:28 | 0 | 0 | 0 | 44.1 | 44.1 | 44.2
2026-08-25T17:02:34 | 0 | 0 | 0 | 44.2 | 44.2 | 44.3
2026-08-25T17:02:39 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:02:44 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:02:49 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:02:54 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:02:59 | 0 | 0 | 0 | 44.2 | 44.1 | 44.3
2026-08-25T17:03:04 | 0 | 0 | 0 | 44.2 | 44.2 | 44.3
2026-08-25T17:03:09 | 0 | 0 | 0 | 44.2 | 44.2 | 44.3
2026-08-25T17:03:14 | 0 | 0 | 0 | 44.2 | 44.1 | 44.2
2026-08-25T17:03:19 | 0 | 0 | 0 | 44.2 | 44.2 | 44.2
2026-08-25T17:03:24 | 0 | 0 | 0 | 44.2 | 44.2 | 44.2
2026-08-25T17:03:29 | 0 | 0 | 0 | 44.2 | 44.1 | 44.2
2026-08-25T17:03:34 | 0 | 0 | 0 | 44.2 | 44.1 | 44.2
2026-08-25T17:03:39 | 0 | 0 | 0 | 44.2 | 44.1 | 44.2
2026-08-25T17:44:04 | 0 | 0 | 0 | 43.6 | 43.6 | 43.6
2026-08-25T17:44:10 | 0 | 0 | 0 | 43.6 | 43.6 | 43.6
2026-08-25T17:44:16 | 0 | 0 | 0 | 43.6 | 43.6 | 43.6
2026-08-25T17:44:21 | 0 | 0 | 0 | 43.5 | 43.6 | 43.6
2026-08-25T17:44:26 | 0 | 0 | 0 | 43.6 | 43.6 | 43.6
2026-08-25T17:44:31 | 0 | 0 | 0 | 43.6 | 43.6 | 43.6
2026-08-25T17:44:36 | 0 | 0 | 0 | 43.6 | 43.6 | 43.7
2026-08-25T17:44:41
2026-08-25T17:44:46
2026-08-25T17:44:52
2026-08-25T17:44:57
2026-08-25T17:45:02
2026-08-25T17:45:08
2026-08-25T17:45:13
2026-08-25T17:45:18
2026-08-25T17:45:24
2026-08-25T17:45:29
2026-08-25T17:45:34
2026-08-25T17:45:40
2026-08-25T17:45:45
2026-08-25T17:45:50
2026-08-25T17:45:56
2026-08-25T17:46:01
2026-08-25T17:46:06
2026-08-25T17:46:12
2026-08-25T17:46:17
2026-08-25T17:46:22
2026-08-25T17:46:29 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:46:34 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:46:39 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:46:44 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:46:49 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:46:54 | 0 | 0 | 0 | 43.8 | 43.8 | 44
2026-08-25T17:46:59 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:47:04 | 0 | 0 | 0 | 43.8 | 43.8 | 44
2026-08-25T17:47:09 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:47:15 | 0 | 0 | 0 | 43.8 | 43.8 | 44
2026-08-25T17:47:20 | 0 | 0 | 0 | 43.8 | 43.9 | 44
2026-08-25T17:47:25 | 0 | 0 | 0 | 43.8 | 43.8 | 43.9
2026-08-25T17:47:30 | 3.3 | 3.3 | 3.3 | 43.8 | 43.8 | 43.9
2026-08-25T17:47:35 | 7.6 | 7.5 | 7.5 | 49.3 | 48.4 | 44.8
2026-08-25T17:47:40 | 7.6 | 7.5 | 7.6 | 53 | 48.5 | 48.6
2026-08-25T17:47:45 | 7.6 | 7.5 | 7.6 | 53.1 | 48.6 | 48.7
2026-08-25T17:47:50 | 7.6 | 7.5 | 7.5 | 31.7 | 37.9 | 38
2026-08-25T17:47:55 | 7.6 | 7.5 | 7.6 | 31.7 | 37.9 | 38.1
2026-08-25T17:48:00 | 7.6 | 7.5 | 7.6 | 31.7 | 37.9 | 38
2026-08-25T17:48:06 | 7.6 | 7.5 | 7.6 | 31.7 | 37.9 | 38
2026-08-25T17:48:11 | 13.5 | 13.4 | 13.5 | 44 | 44 | 44
2026-08-25T17:48:16 | 38.5 | 38.3 | 38.4 | 44 | 44 | 44
2026-08-25T17:48:21 |  |  | 0 | 0 | 0
2026-08-25T17:48:32 | 20.4 | 20.3 | 20.4 | 43.9 | 43.9 | 44
2026-08-25T17:48:35 | 20.3 | 20.3 | 20.3 | 44 | 44 | 44
2026-08-25T17:48:40 | 19.8 | 19.7 | 19.7 | 43.9 | 43.8 | 44
2026-08-25T17:48:45 | 19.6 | 19.5 | 19.5 | 43.8 | 43.8 | 43.9
2026-08-25T17:48:50 | 19 | 18.9 | 19 | 43.9 | 43.8 | 43.9
2026-08-25T17:48:55 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 43.9
2026-08-25T17:49:00 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:49:05 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:10 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:15 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:49:21 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:26 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:31 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:49:36 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:42 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:49:47 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:52 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:49:57 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:02 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:50:07 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:13 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:19 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:24 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:29 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:50:34 | 3.7 | 3.7 | 3.7 | 43.8 | 43.9 | 44
2026-08-25T17:50:39 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:50:44 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:50:49 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:50:54 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:50:59 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:51:05 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:51:10 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:51:15 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:51:20 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:51:25 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:51:30 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:51:35 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:51:40 | 3.7 | 3.7 | 3.7 | 43.8 | 43.9 | 44
2026-08-25T17:51:45 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:51:50 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:51:56 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:52:01 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:06 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:52:11 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:52:16 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:21 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:26 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:32 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:52:37 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:42 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:52:47 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:53 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:52:58 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:03 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:08 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:13 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:18 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:23 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44.1
2026-08-25T17:53:28 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44.1
2026-08-25T17:53:33 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:53:38 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:53:44 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:53:49 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:53:56 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44.1
2026-08-25T17:54:01 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:54:06 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:54:11 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:54:16 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:54:21 | 3.7 | 3.7 | 3.7 | 44 | 43.8 | 44
2026-08-25T17:54:26 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:54:32 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:54:37 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:54:42 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:54:47 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:54:52 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:54:57 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:55:02 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:55:07 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T17:55:12 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44.1
2026-08-25T17:55:17 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:23 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T17:55:28 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:33 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:39 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:55:44 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:49 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:54 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:55:59 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:56:04 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:56:09 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:56:14 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:56:20 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:56:25 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:56:30 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44.1
2026-08-25T17:56:35 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:56:40 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T17:56:45 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:56:50 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:56:55 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:57:00 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:57:05 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:57:11 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:57:16 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:57:21 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44.1
2026-08-25T17:57:26 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:57:31 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:57:36 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:57:41 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44.1
2026-08-25T17:57:46 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44.1
2026-08-25T17:57:51 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44.1
2026-08-25T17:57:57 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44.1
2026-08-25T17:58:03 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:58:08 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:58:13 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:18 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:23 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:28 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:33 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:58:38 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:43 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:48 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:54 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:58:59 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:59:04 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:59:09 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:59:14 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:59:19 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T17:59:24 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:59:29 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:59:34 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T17:59:39 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T17:59:44 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:59:50 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T17:59:55 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:00:00 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:00:05 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:00:11 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:00:16 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:00:21 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.2
2026-08-25T18:00:26 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.2
2026-08-25T18:00:31 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.2
2026-08-25T18:00:36 | 3.7 | 3.7 | 3.7 | 44.1 | 44 | 44.2
2026-08-25T18:00:42 | 3.7 | 3.7 | 3.7 | 44.1 | 44 | 44.2
2026-08-25T18:00:47 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.2
2026-08-25T18:00:52 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.2
2026-08-25T18:00:57 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.2
2026-08-25T18:01:02 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.2
2026-08-25T18:01:07 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:01:12 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:01:17 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:01:22 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:01:27 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.2
2026-08-25T18:01:33 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.2
2026-08-25T18:01:38 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.2
2026-08-25T18:01:43 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:01:48 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.3
2026-08-25T18:01:53 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:01:58 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.2
2026-08-25T18:02:03 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:02:08 | 3.7 | 3.7 | 3.7 | 44.2 | 44.1 | 44.2
2026-08-25T18:02:13 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:02:18 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.2
2026-08-25T18:02:23 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:02:29 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.4
2026-08-25T18:02:34 | 3.7 | 3.7 | 3.7 | 44.3 | 44.2 | 44.4
2026-08-25T18:02:39 | 3.7 | 3.7 | 3.7 | 44.3 | 44.2 | 44.4
2026-08-25T18:02:44 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:02:49 | 3.7 | 3.7 | 3.7 | 44.3 | 44.2 | 44.3
2026-08-25T18:02:54 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.4
2026-08-25T18:02:59 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:03:04 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:03:09 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:03:14 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.3
2026-08-25T18:03:20 | 3.7 | 3.7 | 3.7 | 44.2 | 44.2 | 44.4
2026-08-25T18:03:25 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:03:30 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:03:35 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:03:40 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:03:45 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.6
2026-08-25T18:03:50 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:03:55 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.5
2026-08-25T18:04:00 | 3.7 | 3.7 | 3.7 | 43.4 | 43.4 | 43.4
2026-08-25T18:04:06 | 3.7 | 3.7 | 3.7 | 43.3 | 43.4 | 43.5
2026-08-25T18:04:11 | 3.7 | 3.7 | 3.6 | 43.4 | 43.4 | 43.4
2026-08-25T18:04:16 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:04:22 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:04:28 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:04:33 | 3.6 | 3.6 | 3.6 | 43.2 | 43.3 | 43.3
2026-08-25T18:04:38 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:04:43 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:04:48 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:04:54 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:04:59 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:05:04 | 3.7 | 3.6 | 3.6 | 43.3 | 43.2 | 43.4
2026-08-25T18:05:09 | 3.7 | 3.7 | 3.6 | 43.3 | 43.3 | 43.4
2026-08-25T18:05:14 | 3.7 | 3.7 | 3.6 | 43.3 | 43.2 | 43.4
2026-08-25T18:05:19 | 3.7 | 3.7 | 3.6 | 43.3 | 43.2 | 43.4
2026-08-25T18:05:24 | 3.7 | 3.7 | 3.6 | 43.3 | 43.2 | 43.4
2026-08-25T18:05:29 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:05:34 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:05:39 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:05:45 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:05:50 | 3.7 | 3.6 | 3.6 | 43.3 | 43.2 | 43.4
2026-08-25T18:05:55 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:06:00 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:06:05 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:06:11 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:06:16 | 3.7 | 3.6 | 3.6 | 43.2 | 43.2 | 43.4
2026-08-25T18:06:21
2026-08-25T18:06:26
2026-08-25T18:06:31
2026-08-25T18:06:37
2026-08-25T18:06:42
2026-08-25T18:06:47
2026-08-25T18:06:53
2026-08-25T18:06:58
2026-08-25T18:07:03
2026-08-25T18:07:04 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:07:09
2026-08-25T18:07:11
2026-08-25T18:07:14
2026-08-25T18:07:17
2026-08-25T18:07:19
2026-08-25T18:07:22
2026-08-25T18:07:25
2026-08-25T18:07:27
2026-08-25T18:07:30
2026-08-25T18:07:33
2026-08-25T18:07:35
2026-08-25T18:07:38
2026-08-25T18:07:41
2026-08-25T18:07:43
2026-08-25T18:07:46
2026-08-25T18:07:49
2026-08-25T18:07:51
2026-08-25T18:07:54
2026-08-25T18:07:57
2026-08-25T18:07:59
2026-08-25T18:08:02
2026-08-25T18:08:05
2026-08-25T18:08:07
2026-08-25T18:08:10
2026-08-25T18:08:13
2026-08-25T18:08:15
2026-08-25T18:08:18
2026-08-25T18:08:21
2026-08-25T18:08:23
2026-08-25T18:08:26
2026-08-25T18:08:28
2026-08-25T18:08:31
2026-08-25T18:08:34
2026-08-25T18:08:36
2026-08-25T18:08:39
2026-08-25T18:08:42
2026-08-25T18:08:44
2026-08-25T18:08:47
2026-08-25T18:08:50
2026-08-25T18:08:52
2026-08-25T18:08:55
2026-08-25T18:08:58
2026-08-25T18:09:00
2026-08-25T18:09:03
2026-08-25T18:09:06
2026-08-25T18:09:08
2026-08-25T18:09:11
2026-08-25T18:09:14
2026-08-25T18:09:16
2026-08-25T18:09:19
2026-08-25T18:09:22
2026-08-25T18:09:24
2026-08-25T18:09:27
2026-08-25T18:09:30
2026-08-25T18:09:32
2026-08-25T18:09:35
2026-08-25T18:09:38
2026-08-25T18:09:40
2026-08-25T18:09:43
2026-08-25T18:09:46
2026-08-25T18:09:47 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:09:51
2026-08-25T18:09:52 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:09:56
2026-08-25T18:09:57 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.3
2026-08-25T18:10:02
2026-08-25T18:10:02 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.2
2026-08-25T18:10:07
2026-08-25T18:10:07 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:10:12
2026-08-25T18:10:12 | 3.6 | 3.6 | 3.6 | 43 | 43.1 | 43.2
2026-08-25T18:10:17
2026-08-25T18:10:18
2026-08-25T18:10:23
2026-08-25T18:10:23
2026-08-25T18:10:28
2026-08-25T18:10:28
2026-08-25T18:10:33 | 3.6 | 3.6 | 3.6 | 43 | 43.2 | 43.2
2026-08-25T18:10:33
2026-08-25T18:10:38 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:10:39
2026-08-25T18:10:43 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:10:44
2026-08-25T18:10:48 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:10:49
2026-08-25T18:10:53 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:10:55
2026-08-25T18:10:58 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:11:00
2026-08-25T18:11:03 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.3
2026-08-25T18:11:05
2026-08-25T18:11:08 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:11
2026-08-25T18:11:14 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.2
2026-08-25T18:11:16
2026-08-25T18:11:19 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.2
2026-08-25T18:11:21
2026-08-25T18:11:24 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.3
2026-08-25T18:11:27
2026-08-25T18:11:29 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:32
2026-08-25T18:11:34 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:37
2026-08-25T18:11:39 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:43
2026-08-25T18:11:44 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:48
2026-08-25T18:11:49 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:11:53
2026-08-25T18:11:54 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:11:58
2026-08-25T18:11:59 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:12:04
2026-08-25T18:12:05 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.2
2026-08-25T18:12:09
2026-08-25T18:12:10 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.2
2026-08-25T18:12:14
2026-08-25T18:12:15 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.1
2026-08-25T18:12:20 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.1
2026-08-25T18:12:20
2026-08-25T18:12:25 | 3.6 | 3.6 | 3.6 | 43 | 43 | 43.1
2026-08-25T18:12:25
2026-08-25T18:12:30
2026-08-25T18:12:30 | 3.6 | 3.6 | 3.6 | 43.1 | 43.1 | 43.1
2026-08-25T18:12:36
2026-08-25T18:12:36 | 3.6 | 3.6 | 3.6 | 43.2 | 43.1 | 43.2
2026-08-25T18:12:41
2026-08-25T18:12:41 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:12:46
2026-08-25T18:12:47 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:12:52
2026-08-25T18:12:52 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:12:57
2026-08-25T18:12:58 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:02
2026-08-25T18:13:03 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:08 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:13:08
2026-08-25T18:13:13 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:13
2026-08-25T18:13:18 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:18
2026-08-25T18:13:23 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:24
2026-08-25T18:13:28 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:29
2026-08-25T18:13:33 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:34
2026-08-25T18:13:38 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:39
2026-08-25T18:13:43 | 3.6 | 3.6 | 3.6 | 43.2 | 43.2 | 43.2
2026-08-25T18:13:45
2026-08-25T18:13:50 | 3.6 | 3.6 | 3.6 | 43.1 | 43.2 | 43.2
2026-08-25T18:13:50
2026-08-25T18:13:55 | 3.6 | 3.6 | 3.6 | 43.4 | 43.4 | 43.4
2026-08-25T18:13:55
2026-08-25T18:14:00 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:14:13 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:14:18 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:14:23 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T18:14:29 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:14:34 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:14:39 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 43.8
2026-08-25T18:14:44 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 43.9
2026-08-25T18:14:49 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:14:54 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T18:14:59 | 3.7 | 3.7 | 3.6 | 43.8 | 43.8 | 44
2026-08-25T18:15:04 | 3.7 | 3.6 | 3.6 | 43.8 | 43.8 | 43.9
2026-08-25T18:15:09 | 3.7 | 3.6 | 3.6 | 43.8 | 43.8 | 43.9
2026-08-25T18:15:14 | 3.7 | 3.7 | 3.6 | 43.8 | 43.8 | 43.9
2026-08-25T18:15:20 | 3.7 | 3.7 | 3.7 | 43.8 | 43.8 | 44
2026-08-25T18:15:25 | 3.7 | 3.7 | 3.6 | 43.8 | 43.9 | 43.9
2026-08-25T18:15:30 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:15:35 | 3.7 | 3.7 | 3.6 | 43.9 | 43.9 | 44
2026-08-25T18:15:40 | 3.7 | 3.7 | 3.6 | 43.9 | 43.8 | 43.8
2026-08-25T18:15:45 | 3.7 | 3.7 | 3.6 | 43.8 | 43.8 | 43.8
2026-08-25T18:15:50 | 3.7 | 3.6 | 3.6 | 43.8 | 43.8 | 43.8
2026-08-25T18:15:55 | 3.7 | 3.7 | 3.6 | 43.9 | 43.8 | 43.8
2026-08-25T18:16:00 | 3.7 | 3.7 | 3.6 | 43.9 | 43.8 | 43.8
2026-08-25T18:16:05 | 3.7 | 3.7 | 3.6 | 43.9 | 43.8 | 43.9
2026-08-25T18:16:10 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 43.9
2026-08-25T18:16:16 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:16:21 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T18:16:26 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T18:16:31 | 3.7 | 3.7 | 3.7 | 43.9 | 43.8 | 44
2026-08-25T18:16:37 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:16:42 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:16:47 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:16:52 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:16:57 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:17:03 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:17:08 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:17:13 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:17:18 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:17:23 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:17:28 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:17:33 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:17:38 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:17:43 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:17:48 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:17:54 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T18:17:59 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:04 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:09 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:14 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:19 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:24 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T18:18:29 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:18:34 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:18:39 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44
2026-08-25T18:18:45 | 3.7 | 3.7 | 3.7 | 43.9 | 44 | 44
2026-08-25T18:18:50 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:18:55 | 3.7 | 3.7 | 3.7 | 43.9 | 43.9 | 44
2026-08-25T18:19:00 | 3.7 | 3.7 | 3.7 | 44 | 43.9 | 44
2026-08-25T18:19:05 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:19:10 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:19:15 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.2
2026-08-25T18:19:20 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:19:25 | 3.7 | 3.7 | 3.7 | 44 | 44 | 44.1
2026-08-25T18:19:30 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.1
2026-08-25T18:19:36 | 3.7 | 3.7 | 3.7 | 44.1 | 44 | 44.1
2026-08-25T18:19:41 | 3.7 | 3.7 | 3.7 | 44.1 | 44.1 | 44.1
2026-08-25T18:19:46 | 0 | 0 | 0 | 44 | 44 | 44.1
2026-08-25T18:19:51 | 7.1 | 7 | 7 | 44 | 44 | 44.1
2026-08-25T18:19:56 | 7 | 7 | 7 | 44 | 44 | 44
2026-08-25T18:20:01 | 0 | 0 | 0 | 44 | 44 | 44
2026-08-25T18:20:06 | 0 | 0 | 0 | 43.9 | 43.9 | 44
2026-08-25T18:20:11 | 0 | 0 | 0 | 44 | 43.9 | 44.1
2026-08-25T18:20:16 | 0 | 0 | 0 | 44 | 43.9 | 44.1
2026-08-25T18:20:21 | 0 | 0 | 0 | 44 | 44 | 44.2
2026-08-25T18:20:26 | 0 | 0 | 0 | 44 | 44 | 44.2
2026-08-25T18:20:32 | 19.6 | 19.6 | 19.6 | 44 | 44 | 44.2
2026-08-25T18:20:37 | 13.6 | 13.5 | 13.5 | 44 | 44 | 44.2
2026-08-25T18:20:42 | 13.5 | 13.5 | 13.5 | 44 | 44 | 44.1
2026-08-25T18:20:47 | 13.5 | 13.5 | 13.5 | 44.1 | 44.1 | 44.2
2026-08-25T18:20:52 | 13.5 | 13.5 | 13.5 | 44.2 | 44.1 | 44.2
2026-08-25T18:20:57 | 13.5 | 13.5 | 13.5 | 44.1 | 44 | 44.2
2026-08-25T18:21:02 | 13.5 | 13.5 | 13.5 | 44 | 44 | 44.2
2026-08-25T18:21:07 | 13.5 | 13.4 | 13.5 | 44.1 | 44.1 | 44.1
2026-08-25T18:21:12 | 13.5 | 13.4 | 13.5 | 44.1 | 44.1 | 44.2
2026-08-25T18:21:17 | 13.5 | 13.4 | 13.5 | 44 | 44 | 44.2
2026-08-25T18:21:23 | 13.5 | 13.4 | 13.5 | 44 | 44 | 44.2
2026-08-25T18:21:28 | 13.5 | 13.4 | 13.5 | 44.1 | 44 | 44.2
2026-08-25T18:21:33 | 13.5 | 13.5 | 13.5 | 44.1 | 44.1 | 44.3
2026-08-25T18:21:38 | 13.5 | 13.5 | 13.5 | 44.2 | 44.2 | 44.4
2026-08-25T18:21:43 | 13.5 | 13.5 | 13.5 | 44.2 | 44.2 | 44.3
2026-08-25T18:21:48 | 13.5 | 13.4 | 13.5 | 44.2 | 44.2 | 44.2
2026-08-25T18:21:53 | 13.5 | 13.4 | 13.5 | 44.2 | 44.2 | 44.3
2026-08-25T18:21:58 | 13.5 | 13.4 | 13.5 | 44.2 | 44.2 | 44.3
2026-08-25T18:22:03 | 13.5 | 13.4 | 13.5 | 44.2 | 44.2 | 44.4
2026-08-25T18:22:08 | 13.5 | 13.4 | 13.4 | 44.2 | 44.2 | 44.3
2026-08-25T18:22:13 | 13.5 | 13.4 | 13.4 | 44.1 | 44.2 | 44.3
2026-08-25T18:22:19 | 13.4 | 13.4 | 13.4 | 44.2 | 44.2 | 44.2
2026-08-25T18:22:24 | 13.4 | 13.4 | 13.4 | 44.1 | 44.1 | 44.2
2026-08-25T18:22:29 | 13.4 | 13.4 | 13.4 | 44.1 | 44.1 | 44.2
2026-08-25T18:22:34 | 13.4 | 13.4 | 13.4 | 44.1 | 44.1 | 44.2
2026-08-25T18:22:41 | 13.4 | 13.4 | 13.4 | 442 | 442 | 442
2026-08-25T18:22:46 | 13.4 | 13.4 | 13.4 | 441 | 442 | 442
2026-08-25T18:22:52 | 13.4 | 13.4 | 13.4 | 442 | 442 | 442
2026-08-25T18:22:54 | 13.4 | 13.4 | 13.4 | 44.2 | 44.2 | 44.2
2026-08-25T18:22:59 | 13.4 | 13.4 | 13.4 | 44.2 | 44.2 | 44.2
2026-08-25T18:23:04 | 13.4 | 13.3 | 13.4 | 44.2 | 44.2 | 44.2
2026-08-25T18:23:10 | 13.3 | 13.3 | 13.3 | 44.2 | 44.1 | 44.2
2026-08-25T18:23:15 | 13.4 | 13.3 | 13.3 | 44.2 | 44.1 | 44.2
2026-08-25T18:23:20 | 13.2 | 13.2 | 13.2 | 44.2 | 44.2 | 44.2
2026-08-25T18:23:25 | 13 | 13 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:23:30 | 13 | 13 | 13 | 44.2 | 44.1 | 44.2
2026-08-25T18:23:35 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.1
2026-08-25T18:23:40 | 13 | 12.9 | 13 | 44.1 | 44 | 44.1
2026-08-25T18:23:45 | 13 | 12.9 | 13 | 44 | 44 | 44.1
2026-08-25T18:23:50 | 13 | 12.9 | 13 | 44.1 | 44 | 44
2026-08-25T18:23:55 | 13 | 12.9 | 13 | 44.1 | 44 | 44
2026-08-25T18:24:01 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.1
2026-08-25T18:24:06 | 13 | 12.9 | 13 | 44.1 | 44 | 44.1
2026-08-25T18:24:11 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:24:16 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:24:21 | 13 | 12.9 | 13 | 44 | 44.1 | 44.2
2026-08-25T18:24:26 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:24:31 | 13 | 12.9 | 13 | 44 | 44 | 44.2
2026-08-25T18:24:36 | 13 | 12.9 | 13 | 44 | 44 | 44.2
2026-08-25T18:24:41 | 13 | 12.9 | 13 | 44.1 | 44 | 44.2
2026-08-25T18:24:47 | 13 | 12.9 | 13 | 44 | 44.1 | 44.2
2026-08-25T18:24:53 | 13 | 12.9 | 12.9 | 44 | 44 | 44.1
2026-08-25T18:24:58 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:25:03 | 13 | 12.9 | 13 | 44 | 44.1 | 44.2
2026-08-25T18:25:08 | 13 | 12.9 | 12.9 | 44 | 44.1 | 44.2
2026-08-25T18:25:13 | 13 | 12.9 | 13 | 44 | 44 | 44.2
2026-08-25T18:25:18 | 13 | 12.9 | 13 | 44 | 44.1 | 44.2
2026-08-25T18:25:23 | 13 | 12.9 | 13 | 44 | 44 | 44.2
2026-08-25T18:25:28 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:25:33 | 13 | 12.9 | 13 | 44 | 44 | 44.2
2026-08-25T18:25:38 | 13 | 12.9 | 12.9 | 44 | 44 | 44.1
2026-08-25T18:25:44 | 13 | 12.9 | 12.9 | 44 | 44 | 44.1
2026-08-25T18:25:49 | 13 | 12.9 | 13 | 44 | 44.1 | 44.1
2026-08-25T18:25:54 | 13 | 12.9 | 12.9 | 44 | 44 | 44.1
2026-08-25T18:25:59 | 13 | 12.9 | 12.9 | 44 | 44 | 44.1
2026-08-25T18:26:04 | 13 | 12.9 | 13 | 44 | 44.1 | 44.1
2026-08-25T18:26:09 | 13 | 12.9 | 13 | 44.1 | 44 | 44.1
2026-08-25T18:26:14 | 13 | 12.9 | 13 | 44 | 44.1 | 44.1
2026-08-25T18:26:19 | 13 | 12.9 | 13 | 44 | 44.1 | 44.1
2026-08-25T18:26:24 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.1
2026-08-25T18:26:29 | 13 | 12.9 | 13 | 44.1 | 44.1 | 44.2
2026-08-25T18:26:35 | 13 | 12.9 | 13 | 44.1 | 44.2 | 44.2
2026-08-25T18:26:40 | 13 | 12.9 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:26:45 | 13 | 12.9 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:26:50 | 13 | 12.9 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:26:55 | 13 | 12.9 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:27:00 | 13 | 12.9 | 13 | 44.2 | 44.2 | 44.2
2026-08-25T18:27:06 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:11 | 13 | 12.9 | 13 | 442 | 441 | 442
2026-08-25T18:27:17 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:22 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:27 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:32 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:37 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:42 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:47 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:51 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:27:56 | 13 | 12.9 | 13 | 442 | 442 | 443
2026-08-25T18:28:01 | 13 | 12.9 | 13 | 373 | 372 | 376
2026-08-25T18:28:06 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:28:12 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:28:17 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:28:22 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:28:27 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:28:32 | 13 | 12.9 | 12.9 | 317 | 318 | 319
2026-08-25T18:28:37 | 13 | 12.9 | 12.9 | 317 | 318 | 319
2026-08-25T18:28:42 | 13 | 12.9 | 12.9 | 317 | 318 | 319
2026-08-25T18:28:47 | 13 | 12.9 | 12.9 | 323 | 326 | 323
2026-08-25T18:28:52 | 13 | 12.9 | 13 | 441 | 442 | 443
2026-08-25T18:28:57 | 13 | 12.9 | 13 | 441 | 441 | 443
2026-08-25T18:29:03 | 13 | 12.9 | 13 | 442 | 441 | 442
2026-08-25T18:29:08 | 13 | 12.9 | 13 | 441 | 441 | 442
2026-08-25T18:29:13 | 13 | 12.9 | 13 | 442 | 442 | 442
2026-08-25T18:29:18 | 13 | 12.9 | 13 | 441 | 441 | 442
2026-08-25T18:29:23 | 13 | 12.9 | 13 | 441 | 441 | 442
2026-08-25T18:29:28 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:33 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:38 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:43 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:48 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:54 | 13 | 12.9 | 13 | 441 | 440 | 442
2026-08-25T18:29:59 | 13 | 12.9 | 13 | 442 | 441 | 443
2026-08-25T18:30:04 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:30:09 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:30:14 | 13 | 12.9 | 12.9 | 318 | 318 | 319
2026-08-25T18:30:19 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:30:24 | 13 | 12.9 | 13 | 318 | 318 | 319
2026-08-25T18:30:30 | 13 | 12.9 | 13 | 441 | 442 | 443
2026-08-25T18:30:35 | 13 | 12.9 | 13 | 441 | 442 | 443
2026-08-25T18:30:40 | 13 | 12.9 | 13 | 533 | 533 | 535
2026-08-25T18:30:46 | 13 | 12.9 | 13 | 533 | 533 | 534
2026-08-25T18:30:51 | 13 | 12.9 | 13 | 533 | 533 | 534
2026-08-25T18:30:56 | 13 | 12.9 | 13 | 442 | 441 | 442
2026-08-25T18:31:01 | 13 | 12.9 | 13 | 442 | 441 | 442
2026-08-25T18:31:06 | 28.3 | 28.2 | 28.3 | 442 | 441 | 442
2026-08-25T18:31:11 | 28.5 | 28.4 | 28.4 | 442 | 441 | 442
2026-08-25T18:31:16 | 28.7 | 28.6 | 28.7 | 441 | 440 | 442
2026-08-25T18:31:21 | 28.5 | 28.4 | 28.5 | 441 | 441 | 442
2026-08-25T18:31:26 | 28.3 | 28.3 | 28.3 | 442 | 441 | 442
2026-08-25T18:31:31 | 28.3 | 28.2 | 28.3 | 441 | 440 | 442
2026-08-25T18:31:38 | 28.1 | 28 | 28.1 | 441 | 440 | 442
2026-08-25T18:31:43 | 28.2 | 28.1 | 28.2 | 440 | 441 | 442
2026-08-25T18:31:48 | 28.2 | 28.1 | 28.2 | 440 | 441 | 442
2026-08-25T18:31:53 | 27.9 | 27.8 | 27.9 | 440 | 440 | 442
2026-08-25T18:31:58 | 28.1 | 28.1 | 28.1 | 441 | 441 | 442
2026-08-25T18:32:03 | 28.3 | 28.2 | 28.2 | 441 | 441 | 442
2026-08-25T18:32:08 | 28.2 | 28.2 | 28.2 | 440 | 441 | 443
2026-08-25T18:32:13 | 11.2 | 11.2 | 11.2 | 440 | 441 | 442
2026-08-25T18:32:18 | 11.2 | 11.1 | 11.2 | 440 | 441 | 442
2026-08-25T18:32:23 | 11.2 | 11.1 | 11.2 | 441 | 441 | 442
2026-08-25T18:32:29 | 11.2 | 11.2 | 11.2 | 441 | 441 | 442
2026-08-25T18:32:34 | 11.2 | 11.2 | 11.2 | 442 | 442 | 442
2026-08-25T18:32:39 | 11.2 | 11.2 | 11.2 | 442 | 442 | 442
2026-08-25T18:32:44 | 11.2 | 11.2 | 11.2 | 442 | 442 | 442
2026-08-25T18:32:49 | 11.2 | 11.2 | 11.2 | 441 | 441 | 442
2026-08-25T18:32:54 | 11.2 | 11.2 | 11.2 | 441 | 440 | 442
2026-08-25T18:32:59 | 11.2 | 11.2 | 11.2 | 441 | 441 | 442
2026-08-25T18:33:04 | 11.2 | 11.2 | 11.2 | 440 | 440 | 442
2026-08-25T18:33:09 | 11.2 | 11.2 | 11.2 | 440 | 440 | 442
2026-08-25T18:33:14 | 11.2 | 11.2 | 11.2 | 441 | 441 | 442
2026-08-25T18:33:20 | 11.2 | 11.2 | 11.2 | 441 | 440 | 442
2026-08-25T18:33:25 | 11.2 | 11.2 | 11.2 | 440 | 440 | 442
2026-08-25T18:33:31 | 11.2 | 11.2 | 11.2 | 441 | 441 | 441
2026-08-25T18:33:36 | 11.2 | 11.2 | 11.2 | 440 | 440 | 442
2026-08-25T18:33:41 | 11.2 | 11.2 | 11.2 | 440 | 440 | 442
2026-08-25T18:33:46 | 0 | 0 | 0 | 440 | 440 | 442
2026-08-25T18:33:51 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:33:56 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:01 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:06 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:12 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:17 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:22 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:27 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:32 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:37 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:42 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:47 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:53 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:34:59 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:04 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:09 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:14 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:19 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:24 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:29 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:34 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:39 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:44 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:35:49 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:36:05 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:36:10 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:36:16 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-25T18:36:21 | 0 | 0 | 0 | 0 | 0 | 0
2026-08-26T16:43:27 | 5.57 | 4.76 | 5.16 | 411.3 | 413 | 411.2 | 51.36 | 8.4 | 20.05 | 80.43 | 35.54 | 88.69 | 4.72 | 4.95 | 5.02 | 1 | 1 | 1 | 0
2026-08-26T16:43:32 | 5.26 | 5.16 | 4.81 | 410.3 | 420.3 | 419 | 44 | 90.34 | 94.7 | 99.61 | 12.78 | 34.59 | 5.07 | 4.56 | 4.67 | 0 | 0 | 1 | 1
2026-08-26T16:43:37 | 5.37 | 4.51 | 5.62 | 417.3 | 409.4 | 410.7 | 65.02 | 58.63 | 62.27 | 99.13 | 22.56 | 73.28 | 4.73 | 5.44 | 4.53 | 0 | 0 | 1 | 1
2026-08-26T16:43:42 | 5.36 | 4.64 | 4.64 | 415.5 | 418 | 409.2 | 70.65 | 29.18 | 74.68 | 27.78 | 68.3 | 94.53 | 5.26 | 4.69 | 4.76 | 0 | 0 | 1 | 1
2026-08-26T16:43:47 | 5.19 | 4.66 | 5.69 | 414.4 | 414.6 | 414.2 | 76.8 | 54.83 | 27.87 | 85.64 | 32.54 | 29.15 | 5.12 | 5.52 | 4.7 | 0 | 0 | 1 | 0
2026-08-26T16:43:52 | 5.54 | 5.58 | 5.64 | 419.7 | 419.9 | 418.2 | 96.52 | 0.73 | 26.62 | 44.71 | 5.59 | 63.75 | 5.17 | 5.5 | 5.1 | 1 | 1 | 1 | 0
2026-08-26T16:43:57 | 4.79 | 5.64 | 5.39 | 415 | 408.2 | 418 | 69.41 | 98.66 | 12.08 | 96.08 | 21.97 | 8.31 | 5.41 | 4.74 | 5.11 | 1 | 0 | 1 | 1
2026-08-26T16:44:02 | 4.86 | 4.5 | 4.78 | 419.4 | 415.1 | 416.5 | 1.86 | 92.59 | 87.97 | 36.57 | 64.36 | 29.64 | 5.42 | 5.06 | 4.78 | 0 | 0 | 1 | 1
2026-08-26T16:44:07 | 4.71 | 5.47 | 5.21 | 419.1 | 420.1 | 412 | 98.52 | 91.96 | 43.87 | 71.17 | 29.16 | 94.71 | 5.21 | 5.47 | 5.61 | 0 | 0 | 1 | 0
2026-08-26T16:44:12 | 5.4 | 5.54 | 4.54 | 408.3 | 414.1 | 419.5 | 67.25 | 98.73 | 54.57 | 39.56 | 21.92 | 19.9 | 5.02 | 4.82 | 5.45 | 1 | 0 | 1 | 0
2026-08-26T16:44:17 | 4.6 | 4.69 | 5.29 | 414.1 | 409.6 | 420.4 | 31.04 | 10.65 | 59.48 | 95.27 | 43.05 | 66.73 | 5.15 | 5.29 | 5.45 | 1 | 0 | 1 | 1
2026-08-26T16:44:22 | 5.03 | 5.01 | 4.74 | 415.7 | 409.1 | 415.3 | 58.66 | 79.85 | 79.06 | 71.15 | 61.11 | 83.57 | 5.56 | 5.06 | 4.71 | 0 | 0 | 1 | 0
2026-08-26T16:44:27 | 5.24 | 5.64 | 5.6 | 411.6 | 417.6 | 409.8 | 42.24 | 52.24 | 33.02 | 91.51 | 29.76 | 20.3 | 4.98 | 5.12 | 5.49 | 1 | 1 | 0 | 0
2026-08-26T16:44:32 | 5.19 | 5.14 | 5.34 | 412.3 | 409.9 | 417.3 | 85.75 | 26.26 | 13.53 | 49.35 | 69.07 | 70.96 | 4.6 | 4.51 | 5.64 | 1 | 0 | 1 | 0
2026-08-26T16:44:37 | 5.47 | 5.64 | 4.53 | 414.3 | 411.9 | 409.7 | 70.49 | 57.65 | 25.51 | 81.22 | 15.13 | 42.14 | 5.38 | 4.74 | 4.53 | 1 | 0 | 0 | 0
2026-08-26T16:44:42 | 4.95 | 5.29 | 5.4 | 421.9 | 412.5 | 418.2 | 60.72 | 21.19 | 92.09 | 9.83 | 66.5 | 51.22 | 5.54 | 5.33 | 4.82 | 0 | 0 | 1 | 0
2026-08-26T16:44:47 | 4.54 | 4.72 | 5.49 | 408.7 | 417.2 | 417.1 | 38.02 | 34.09 | 82.13 | 80.24 | 86.89 | 50.83 | 5.16 | 4.55 | 5.57 | 0 | 0 | 1 | 1
2026-08-26T16:44:52 | 4.92 | 5.01 | 5.59 | 414 | 411.7 | 415.8 | 74.55 | 71.18 | 26.26 | 57.79 | 65.07 | 26.15 | 4.98 | 4.84 | 5.4 | 1 | 1 | 0 | 0
2026-08-26T16:44:57 | 5.14 | 5.38 | 5 | 415.8 | 420.8 | 408.4 | 19.95 | 52.26 | 66.82 | 5.43 | 25.26 | 53.07 | 5.47 | 4.92 | 5.3 | 1 | 0 | 1 | 1
2026-08-26T16:45:02 | 5.02 | 4.99 | 4.58 | 413.5 | 416.5 | 408.5 | 86.32 | 31.23 | 85.02 | 51.17 | 2.15 | 41.57 | 4.85 | 4.56 | 5.7 | 1 | 0 | 1 | 0
2026-08-26T16:45:07 | 5 | 5.23 | 5.07 | 414.1 | 413 | 419 | 48.81 | 27.4 | 92.58 | 82.5 | 46 | 52.59 | 5.34 | 5.31 | 4.75 | 1 | 1 | 0 | 0
2026-08-26T16:45:12 | 5.7 | 5.55 | 5.1 | 417.5 | 408.7 | 416.8 | 9.21 | 68.61 | 90.89 | 54.41 | 68.18 | 61.32 | 4.74 | 4.95 | 4.76 | 1 | 0 | 1 | 1
2026-08-26T16:45:17 | 4.88 | 5.44 | 4.88 | 414.5 | 412 | 419.4 | 98.84 | 17.48 | 21.01 | 8.54 | 46.88 | 93.39 | 5.61 | 5.46 | 4.93 | 0 | 0 | 1 | 0
2026-08-26T16:45:22 | 4.9 | 4.72 | 4.87 | 414.3 | 410.3 | 418.7 | 68.62 | 87.41 | 4.53 | 23.69 | 59.34 | 84.38 | 4.68 | 4.71 | 5.45 | 1 | 0 | 1 | 1
2026-08-26T16:45:27 | 4.82 | 4.74 | 5.42 | 421.6 | 419.3 | 419.8 | 99.67 | 42.87 | 98.02 | 41.28 | 89.64 | 78.46 | 5.64 | 4.8 | 5.52 | 1 | 0 | 1 | 0
2026-08-26T16:45:32 | 5.46 | 5.37 | 5.14 | 410.7 | 421.3 | 413.1 | 7.1 | 65.61 | 17.22 | 79.12 | 61.86 | 26.79 | 5.66 | 4.55 | 4.83 | 0 | 0 | 1 | 0
2026-08-26T16:45:37 | 5.56 | 5.52 | 4.54 | 412.3 | 422 | 414.3 | 34.64 | 55.78 | 79.3 | 12.14 | 40.87 | 85.96 | 5.11 | 5.14 | 5.17 | 1 | 0 | 1 | 0
2026-08-26T16:45:53 | 5.13 | 5.12 | 4.95 | 421.5 | 410.4 | 416 | 7.7 | 21.4 | 557.3 | 166.5 | 27 | 50.9 | 7.3 | 6.2 | 2.5 | 1 | 0 | 1 | 1
2026-08-26T16:45:58 | 5.53 | 4.75 | 5.07 | 411.2 | 416 | 415.3 | 10.3 | 15.3 | 196.3 | 553.8 | 59.2 | 24.1 | 8.4 | 6.7 | 3.1 | 0 | 0 | 1 | 1
2026-08-26T16:46:03 | 4.79 | 5.67 | 5.34 | 420.6 | 421.7 | 421.3 | 32.8 | 27.1 | 579.7 | 576.5 | 36 | 57.1 | 7.3 | 6.1 | 2.4 | 1 | 0 | 0 | 0
2026-08-26T16:46:08 | 5.46 | 4.94 | 5.51 | 415.7 | 418.3 | 420.8 | 15.6 | 24.8 | 265.7 | 548.4 | 50.6 | 25.8 | 7.7 | 6.6 | 2.9 | 1 | 1 | 0 | 0
2026-08-26T16:46:13 | 4.51 | 5.44 | 5.65 | 419.8 | 412.9 | 415 | 27.5 | 39.4 | 319.1 | 218.5 | 22.2 | 34.5 | 7.1 | 7.7 | 2.7 | 1 | 0 | 1 | 0
2026-08-26T16:46:18 | 4.89 | 4.8 | 4.69 | 408.4 | 411.7 | 410.9 | 42.4 | 36.5 | 412.4 | 571.2 | 14.9 | 58.5 | 6.4 | 8.5 | 3 | 0 | 0 | 1 | 0
2026-08-26T16:46:23 | 4.64 | 5.34 | 5.59 | 411.5 | 414.8 | 411.1 | 18.7 | 37.9 | 260.5 | 202.9 | 48.3 | 53.2 | 8.3 | 8.3 | 2.7 | 1 | 0 | 1 | 0
2026-08-26T16:46:28 | 4.53 | 5.26 | 4.97 | 415.5 | 420.9 | 409.1 | 25.6 | 18 | 244.8 | 306.4 | 12 | 49.1 | 6.2 | 6.8 | 2.3 | 0 | 0 | 1 | 0
2026-08-26T16:46:33 | 5.1 | 5.35 | 4.71 | 414.2 | 416.3 | 411.1 | 23.6 | 19.5 | 512.7 | 421.4 | 39.3 | 10.1 | 6.3 | 8.3 | 2.8 | 0 | 0 | 1 | 1
2026-08-26T16:46:38 | 5.14 | 5.25 | 5.54 | 415.9 | 420.6 | 417.6 | 7.5 | 12.5 | 431.8 | 202 | 37.8 | 45.3 | 6.3 | 7.8 | 2 | 0 | 0 | 1 | 1
2026-08-26T16:46:43 | 5.09 | 5.29 | 4.7 | 421.5 | 421.1 | 419.5 | 29.9 | 27.5 | 133.3 | 143.7 | 52.8 | 10.4 | 6.4 | 7.6 | 3.4 | 1 | 1 | 1 | 0
2026-08-26T16:46:48 | 4.86 | 4.9 | 4.65 | 417.4 | 413.1 | 415 | 8.3 | 31.3 | 122.1 | 261.9 | 31.7 | 12.9 | 7.9 | 6.5 | 3 | 1 | 0 | 1 | 1
2026-08-26T16:46:53 | 4.68 | 4.73 | 5.45 | 418.9 | 420.4 | 409.9 | 28.7 | 16.2 | 180.7 | 535 | 41.2 | 45.9 | 6.3 | 6.7 | 3 | 1 | 1 | 1 | 1
2026-08-26T16:46:58 | 4.74 | 4.52 | 5.59 | 416.4 | 418.3 | 420.2 | 33.9 | 26.3 | 413.2 | 403.7 | 49.7 | 56.7 | 8.3 | 7.8 | 2.2 | 0 | 0 | 1 | 1
2026-08-26T16:47:03 | 5.12 | 5.57 | 4.92 | 418.4 | 418.2 | 413.4 | 43.5 | 35.1 | 561.5 | 200.9 | 14.1 | 46.5 | 7.8 | 6.1 | 2.3 | 0 | 0 | 0 | 0
2026-08-26T16:47:08 | 4.56 | 4.96 | 4.98 | 408.9 | 410.2 | 420.4 | 31.1 | 17.3 | 263.2 | 563.2 | 49.2 | 36.2 | 8.4 | 7.4 | 2.8 | 0 | 0 | 0 | 0
2026-08-26T16:47:13 | 5.55 | 5.55 | 5.51 | 408.2 | 416.2 | 418.1 | 11 | 22.8 | 348.7 | 452.2 | 17.3 | 33.6 | 6.3 | 7.6 | 2.9 | 1 | 1 | 0 | 0
2026-08-26T16:47:18 | 5.03 | 5.58 | 4.6 | 414 | 413.7 | 413.4 | 14.6 | 38.8 | 399.4 | 183.8 | 38.7 | 46 | 7.2 | 7.2 | 2 | 1 | 0 | 0 | 0
2026-08-26T16:47:23 | 5.59 | 5.29 | 4.63 | 419 | 409 | 416.4 | 29 | 5.9 | 519.7 | 573.7 | 20.5 | 15.5 | 7.3 | 7.6 | 3.2 | 0 | 0 | 1 | 1
2026-08-26T16:47:29 | 5.05 | 5.05 | 4.8 | 415.1 | 411.1 | 413.7 | 39.7 | 33.5 | 189.4 | 443.5 | 29.8 | 14.4 | 6.3 | 6.5 | 3.5 | 0 | 0 | 1 | 0
2026-08-26T16:47:34 | 4.84 | 5.11 | 5.45 | 420.8 | 415.5 | 419.3 | 43.4 | 11.8 | 147.9 | 502.7 | 18.6 | 45.3 | 7.3 | 6.5 | 2.1 | 1 | 0 | 1 | 0
2026-08-26T16:47:39 | 5.04 | 4.85 | 4.64 | 411.5 | 411.7 | 421.1 | 15 | 31.8 | 342.5 | 338.1 | 56.2 | 25 | 6 | 8 | 2.4 | 1 | 0 | 1 | 0
2026-08-26T16:47:44 | 5.18 | 5.3 | 5.59 | 409 | 411.1 | 410.1 | 38.4 | 17.5 | 413.5 | 513.7 | 48.8 | 40.3 | 7.1 | 7.6 | 3.3 | 0 | 0 | 1 | 0
2026-08-26T16:47:49 | 5.37 | 5.15 | 5.45 | 421.9 | 409.7 | 412.8 | 14.4 | 11.7 | 586.1 | 454.9 | 43.4 | 16.8 | 7.1 | 6.5 | 2.7 | 0 | 0 | 1 | 1
2026-08-26T16:47:54 | 5.55 | 4.78 | 5.44 | 408.4 | 420.9 | 422 | 42.4 | 37.2 | 197.7 | 423.1 | 29.7 | 38.9 | 7.1 | 7.9 | 2 | 0 | 0 | 0 | 0
2026-08-26T16:47:59 | 4.63 | 4.81 | 5.15 | 409.5 | 419.3 | 410 | 21.8 | 7.7 | 252 | 172.1 | 22.2 | 27.2 | 6.4 | 8.2 | 3.3 | 1 | 0 | 1 | 1
2026-08-26T16:48:04 | 5.24 | 5.43 | 4.89 | 410.5 | 413.1 | 408.9 | 11.3 | 41.2 | 565.1 | 349 | 18.8 | 55.9 | 6.6 | 6.7 | 2.9 | 1 | 1 | 1 | 1
2026-08-26T16:48:09 | 4.66 | 5.28 | 5.29 | 409 | 418.1 | 419.1 | 34.7 | 41.1 | 159.5 | 520.1 | 45.6 | 39.6 | 6.7 | 6.5 | 2.5 | 1 | 0 | 1 | 0
2026-08-26T16:48:14 | 4.78 | 5.49 | 5.62 | 408.8 | 415.6 | 417.6 | 20.1 | 26.2 | 317.8 | 283.1 | 45.1 | 29.5 | 7.6 | 7 | 2.9 | 0 | 0 | 0 | 0
2026-08-26T16:48:19 | 5.23 | 4.85 | 5.07 | 411.6 | 416.6 | 410.1 | 21.3 | 21 | 292.7 | 596.1 | 12.6 | 38.1 | 7.9 | 7.4 | 2.7 | 1 | 0 | 0 | 0
2026-08-26T16:48:24 | 4.75 | 5.15 | 5.02 | 412.7 | 411.5 | 412.5 | 34.1 | 23.2 | 303.1 | 470.9 | 21.6 | 43.4 | 7.2 | 8 | 2.6 | 1 | 0 | 1 | 1
2026-08-26T16:48:29 | 5.51 | 5.63 | 4.94 | 410.4 | 417.7 | 417.4 | 27.3 | 36.1 | 319.8 | 274.8 | 56 | 47.5 | 7.8 | 6.7 | 3.1 | 1 | 1 | 1 | 1
2026-08-26T16:48:34 | 5.32 | 5.05 | 5.24 | 410.3 | 419.2 | 419 | 7.9 | 9.9 | 198.2 | 497.1 | 23.4 | 49.6 | 7.2 | 8.2 | 2.1 | 1 | 0 | 1 | 1
2026-08-26T16:48:39 | 5.53 | 5.07 | 5.03 | 412.8 | 419.6 | 415.1 | 34.2 | 37.3 | 440.1 | 121.6 | 33.6 | 45.1 | 7.3 | 6.8 | 3.4 | 1 | 0 | 1 | 0
2026-08-26T16:48:44 | 4.69 | 5.67 | 4.93 | 416.9 | 414.3 | 415.6 | 8.4 | 25.8 | 208.8 | 391.4 | 44.2 | 42.2 | 6.2 | 6.6 | 2 | 0 | 0 | 0 | 0
2026-08-26T16:48:49 | 4.78 | 5.49 | 5.38 | 415.1 | 412.1 | 409.8 | 32.9 | 8.7 | 322.6 | 340.2 | 27 | 37.7 | 7 | 6.5 | 2.8 | 1 | 1 | 0 | 0
2026-08-26T16:48:54 | 5.02 | 4.79 | 5.31 | 410.9 | 411 | 418.9 | 29.9 | 31.1 | 416.5 | 580.1 | 26.9 | 43 | 8.1 | 7.4 | 2.9 | 0 | 0 | 0 | 0
2026-08-26T16:48:59 | 5.07 | 5.2 | 5.12 | 412.4 | 417.3 | 419.8 | 33.2 | 12.3 | 185.3 | 402.9 | 18.9 | 36.3 | 7 | 6.2 | 3.1 | 1 | 1 | 1 | 1
2026-08-26T16:49:04 | 5.32 | 5.07 | 4.5 | 420.7 | 412.4 | 413.6 | 35.7 | 20.2 | 498.9 | 212.2 | 12.4 | 32.3 | 8 | 7.2 | 2.1 | 1 | 1 | 1 | 1
2026-08-26T16:49:09 | 5.56 | 5.38 | 4.89 | 410.6 | 416.9 | 419.3 | 42.1 | 37.5 | 272.3 | 452.7 | 32.6 | 43.8 | 6.1 | 6.9 | 2.2 | 1 | 1 | 1 | 0
2026-08-26T16:49:14 | 4.67 | 5.1 | 4.69 | 419.4 | 417.9 | 421 | 41.4 | 32 | 243.5 | 234.4 | 10 | 25.9 | 6.9 | 6.2 | 2.5 | 1 | 0 | 1 | 0
2026-08-26T16:49:19 | 5.13 | 4.91 | 4.84 | 408.8 | 421.9 | 421.3 | 40 | 18 | 320.8 | 263 | 21.9 | 14.3 | 6.8 | 6.7 | 3.2 | 0 | 0 | 1 | 0
2026-08-26T16:49:24 | 4.55 | 4.72 | 5.5 | 415.4 | 411.8 | 411.3 | 19.5 | 27 | 575.5 | 530.4 | 10.6 | 21.6 | 8.4 | 8.1 | 2.2 | 1 | 1 | 1 | 1
2026-08-26T16:49:29 | 5.6 | 5.13 | 4.84 | 413.8 | 419.8 | 411.1 | 5.8 | 32.8 | 202.5 | 289.9 | 39 | 52.8 | 6.1 | 6.5 | 2.2 | 1 | 1 | 1 | 0
2026-08-26T16:49:34 | 5.42 | 5.69 | 5.44 | 418.3 | 414.5 | 418.5 | 34 | 42.7 | 397.7 | 248.9 | 50.7 | 21.4 | 6 | 8.2 | 2.9 | 1 | 0 | 0 | 0
2026-08-26T16:49:39 | 5.59 | 4.96 | 4.98 | 420.6 | 421.1 | 414.7 | 39.5 | 9.6 | 469.8 | 553.4 | 40.3 | 16.8 | 8.3 | 7 | 3.3 | 1 | 1 | 1 | 1
2026-08-26T16:49:44 | 4.5 | 5.68 | 5.17 | 419.3 | 408.7 | 419.7 | 20 | 5.3 | 575.9 | 580 | 27.1 | 31 | 7.1 | 7.9 | 2.1 | 1 | 1 | 0 | 0
2026-08-26T16:49:49 | 5.56 | 4.84 | 5.37 | 410.2 | 418.8 | 416.5 | 12.5 | 11.2 | 265.2 | 353.3 | 27.1 | 60 | 6.1 | 7.3 | 2.9 | 1 | 0 | 0 | 0
2026-08-26T16:49:54 | 5.55 | 4.71 | 4.73 | 408.3 | 415.3 | 414.3 | 6.4 | 44.9 | 525.1 | 146.4 | 55.4 | 21 | 6.9 | 6.3 | 2.8 | 0 | 0 | 1 | 1
2026-08-26T16:49:59 | 4.98 | 5.22 | 5.01 | 416 | 421.5 | 408.2 | 21.4 | 37.9 | 579.9 | 247.7 | 55.1 | 41.3 | 8.4 | 7.8 | 2.1 | 0 | 0 | 1 | 0
2026-08-26T16:50:04 | 5.27 | 5.54 | 4.75 | 410.5 | 417.1 | 413.9 | 35.1 | 25 | 134.5 | 428.3 | 42.7 | 11.9 | 8.4 | 6.3 | 3.2 | 1 | 0 | 1 | 0
2026-08-26T16:50:09 | 5.53 | 4.96 | 5.47 | 420.6 | 419.5 | 416.5 | 43 | 30.3 | 141.3 | 565.5 | 10 | 10.7 | 7.7 | 8.1 | 2.1 | 0 | 0 | 1 | 1
2026-08-26T16:50:14 | 5.53 | 4.68 | 4.72 | 421.1 | 415.5 | 414.5 | 35.1 | 17.3 | 154.7 | 407.9 | 17.5 | 41.2 | 7.2 | 7.7 | 2.7 | 1 | 0 | 1 | 0
2026-08-26T16:50:19 | 4.82 | 4.91 | 4.98 | 414.9 | 410.9 | 413.2 | 41.9 | 33.2 | 198.1 | 511.4 | 59.7 | 29.9 | 7.2 | 8.4 | 3.2 | 1 | 0 | 1 | 0
2026-08-26T16:50:24 | 5.45 | 4.58 | 5.35 | 418.7 | 409.7 | 417.5 | 37.6 | 8.4 | 419.1 | 377.7 | 23.7 | 26.3 | 6.4 | 6.6 | 3.2 | 0 | 0 | 0 | 0
2026-08-26T16:50:29 | 5.14 | 5.22 | 4.73 | 416.7 | 411.2 | 416.1 | 34.5 | 39.2 | 228.4 | 352.8 | 10.2 | 23.1 | 7.4 | 7.7 | 3.4 | 1 | 0 | 0 | 0
2026-08-26T16:50:34 | 4.68 | 4.55 | 4.54 | 418.5 | 420.5 | 419.3 | 29.4 | 32.3 | 317.5 | 135.2 | 27.5 | 22.1 | 7.9 | 6.7 | 2.5 | 1 | 1 | 1 | 1
2026-08-26T16:50:39 | 5.32 | 4.92 | 4.98 | 408.4 | 412.5 | 408.9 | 29.6 | 39.4 | 460.1 | 439.5 | 54.3 | 41 | 7 | 6.2 | 3.4 | 0 | 0 | 1 | 1
2026-08-26T16:50:44 | 5.06 | 5.5 | 5.02 | 413.8 | 413.5 | 418.5 | 28.6 | 13.8 | 555.2 | 122.4 | 27.8 | 34.4 | 7 | 7.1 | 2.5 | 1 | 1 | 1 | 0
2026-08-26T16:50:49 | 5.07 | 4.84 | 4.65 | 412.6 | 415.9 | 416 | 35.2 | 32.7 | 439.6 | 314.8 | 33.7 | 34.9 | 7.7 | 6 | 3.3 | 1 | 1 | 0 | 0
2026-08-26T16:50:54 | 5.12 | 5.06 | 5.36 | 420.7 | 412.6 | 409.1 | 7.5 | 20.3 | 550.7 | 469.9 | 18 | 40.2 | 8.1 | 6.2 | 2.3 | 0 | 0 | 1 | 1
2026-08-26T16:50:59 | 5 | 5.46 | 4.57 | 413.2 | 413.2 | 419.4 | 6.1 | 31.6 | 307.8 | 236.7 | 26.8 | 52.7 | 6 | 8 | 2.1 | 0 | 0 | 1 | 0
2026-08-26T16:51:04 | 5.28 | 5.18 | 4.82 | 414.5 | 413.3 | 421.9 | 32.6 | 30.8 | 576.3 | 509.4 | 15.6 | 34.2 | 7.8 | 8 | 2.9 | 1 | 0 | 0 | 0
2026-08-26T16:51:09 | 5.31 | 5.43 | 4.69 | 419.6 | 413.2 | 414.7 | 27.5 | 8.2 | 231.8 | 370.8 | 55 | 53.7 | 7.3 | 6.9 | 3.3 | 0 | 0 | 1 | 0
2026-08-26T16:51:14 | 5.63 | 4.83 | 4.66 | 417.7 | 421.9 | 411.7 | 38.1 | 6.7 | 526.5 | 325.3 | 24.5 | 19.1 | 6.8 | 7 | 2.9 | 0 | 0 | 1 | 1
2026-08-26T16:51:19 | 5.12 | 5.62 | 4.62 | 419.3 | 417.7 | 413.7 | 14.4 | 26.5 | 505.6 | 332.1 | 55.9 | 18.5 | 7.9 | 7.6 | 2.2 | 1 | 1 | 0 | 0
2026-08-26T16:51:24 | 5.62 | 4.96 | 5.08 | 416.1 | 409.3 | 415.6 | 24.7 | 31.3 | 206.1 | 243.1 | 59.1 | 10.9 | 6.1 | 8 | 2.9 | 1 | 0 | 1 | 0
2026-08-26T16:51:29 | 5.17 | 5.44 | 4.76 | 415.8 | 412.8 | 411.7 | 43.4 | 17.5 | 387.4 | 297.4 | 27.2 | 22.5 | 6.9 | 6.5 | 2.4 | 0 | 0 | 1 | 1
2026-08-26T17:02:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:02:37 | 4.2 | 4.2 | 4.2 | 455 | 464 | 467 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:02:42 | 7.4 | 7.4 | 7.4 | 460 | 470 | 473 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:02:48 | 7.3 | 7.3 | 7.3 | 456 | 466 | 469 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:02:53 | 7.3 | 7.3 | 7.3 | 455 | 466 | 468 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:02:58 | 7.3 | 7.2 | 7.3 | 452 | 462 | 464 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:03 | 7.3 | 7.2 | 7.3 | 452 | 462 | 464 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:08 | 7.3 | 7.2 | 7.3 | 452 | 462 | 464 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:14 | 7.3 | 7.2 | 7.3 | 453 | 462 | 464 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:19 | 7.3 | 7.3 | 7.3 | 455 | 465 | 468 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:24 | 7.3 | 7.3 | 7.3 | 456 | 466 | 469 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:29 | 7.4 | 7.4 | 7.4 | 461 | 472 | 473 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:34 | 7.4 | 7.4 | 7.4 | 460 | 470 | 472 | 0 | 6 | 0 | 0 | 0 | 0.6 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:40 | 7.4 | 7.3 | 7.4 | 458 | 467 | 469 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:45 | 7.3 | 7.3 | 7.3 | 455 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:50 | 7.3 | 7.3 | 7.3 | 455 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:03:55 | 7.3 | 7.3 | 7.3 | 455 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:00 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:05 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:11 | 7.3 | 7.3 | 7.3 | 454 | 463 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:16 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:22 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:27 | 7.3 | 7.3 | 7.3 | 453 | 464 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:32 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 7 | 0 | 0 | 0 | 0.1 | 18 | 40 | 0 | 0 | 250 | 0 | 102
2026-08-26T17:04:38 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:04:44 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:04:49 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:04:54 | 7.3 | 7.3 | 7.3 | 455 | 465 | 467 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:04:59 | 7.3 | 7.2 | 7.3 | 451 | 462 | 464 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:05:04 | 7.3 | 7.2 | 7.3 | 450 | 460 | 463 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 0 | 0 | 0
2026-08-26T17:05:09 | 7.3 | 7.2 | 7.3 | 450 | 460 | 463 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 0 | 0 | 0
2026-08-26T17:05:15 | 7.3 | 7.2 | 7.3 | 450 | 461 | 463 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:05:20 | 7.3 | 7.2 | 7.2 | 450 | 460 | 462 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 1 | 1
2026-08-26T17:05:25 | 7.2 | 7.2 | 7.2 | 449 | 459 | 462 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 1 | 1
2026-08-26T17:05:30 | 7.3 | 7.3 | 7.3 | 455 | 465 | 468 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:05:35 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:05:41 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:05:46 | 7.4 | 7.4 | 7.4 | 461 | 471 | 474 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:05:51 | 7.4 | 7.4 | 7.4 | 459 | 469 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:05:56 | 7.4 | 7.3 | 7.4 | 458 | 468 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:01 | 7.4 | 7.4 | 7.4 | 459 | 469 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:06 | 7.4 | 7.4 | 7.4 | 458 | 468 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:12 | 7.4 | 7.4 | 7.4 | 458 | 468 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:17 | 7.4 | 7.3 | 7.4 | 457 | 468 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:22 | 7.3 | 7.3 | 7.3 | 453 | 463 | 465 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 1
2026-08-26T17:06:27 | 7.3 | 7.3 | 7.3 | 453 | 462 | 465 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:32 | 7.3 | 7.3 | 7.3 | 453 | 462 | 464 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:38 | 7.3 | 7.3 | 7.3 | 452 | 461 | 464 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:43 | 7.3 | 7.3 | 7.3 | 453 | 462 | 465 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:48 | 7.3 | 7.3 | 7.3 | 453 | 462 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:53 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:06:58 | 7.3 | 7.3 | 7.3 | 453 | 462 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:04 | 7.3 | 7.3 | 7.3 | 453 | 464 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:09 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:14 | 7.3 | 7.3 | 7.3 | 453 | 463 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 1 | 0 | 0
2026-08-26T17:07:19 | 7.3 | 7.3 | 7.3 | 454 | 464 | 466 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:24 | 7.3 | 7.3 | 7.3 | 455 | 465 | 468 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:29 | 7.3 | 7.3 | 7.3 | 455 | 465 | 467 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:35 | 7.3 | 7.3 | 7.3 | 456 | 465 | 468 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:41 | 7.4 | 7.4 | 7.4 | 459 | 469 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:46 | 7.4 | 7.3 | 7.4 | 457 | 468 | 469 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:53 | 7.4 | 7.3 | 7.4 | 457 | 468 | 470 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:07:58 | 7.4 | 7.3 | 7.4 | 458 | 469 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:03 | 7.4 | 7.3 | 7.4 | 458 | 468 | 470 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:09 | 7.4 | 7.4 | 7.4 | 459 | 469 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:14 | 7.4 | 7.4 | 7.4 | 459 | 470 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:19 | 7.4 | 7.4 | 7.4 | 460 | 471 | 473 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:25 | 7.4 | 7.4 | 7.4 | 459 | 471 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:30 | 7.4 | 7.4 | 7.4 | 460 | 472 | 473 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:35 | 7.4 | 7.4 | 7.4 | 461 | 472 | 473 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:40 | 7.4 | 7.4 | 7.4 | 459 | 471 | 473 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:47 | 7.4 | 7.4 | 7.4 | 459 | 471 | 473 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:52 | 7.4 | 7.4 | 7.4 | 459 | 470 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:08:58 | 7.4 | 7.4 | 7.4 | 459 | 471 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:03 | 7.4 | 7.4 | 7.4 | 459 | 471 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:08 | 7.4 | 7.4 | 7.4 | 459 | 471 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:14 | 7.4 | 7.4 | 7.4 | 459 | 471 | 472 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:19 | 7.3 | 7.2 | 7.3 | 451 | 462 | 463 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:24 | 7.3 | 7.2 | 7.3 | 451 | 461 | 462 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 0 | 0 | 0 | 0
2026-08-26T17:09:29 | 7.4 | 7.3 | 7.4 | 458 | 469 | 471 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:09:34 | 7.5 | 7.4 | 7.5 | 463 | 475 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:09:39 | 7.5 | 7.5 | 7.5 | 465 | 476 | 478 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:09:45 | 7.5 | 7.5 | 7.5 | 465 | 475 | 478 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:09:50 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:09:55 | 9.1 | 9 | 9.1 | 462 | 473 | 475 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:00 | 9.1 | 9.1 | 9.1 | 464 | 474 | 476 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:05 | 9.1 | 9.1 | 9.1 | 465 | 475 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:11 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:16 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:21 | 9.1 | 9.1 | 9.1 | 463 | 474 | 477 | 0 | 8 | 0 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:29 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:34 | 9.1 | 9 | 9.1 | 461 | 473 | 475 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:40 | 9.1 | 9.1 | 9.1 | 463 | 474 | 477 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:45 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:51 | 9.1 | 9 | 9.1 | 461 | 471 | 474 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:10:56 | 9.1 | 9 | 9.1 | 461 | 471 | 474 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:01 | 9.1 | 9 | 9.1 | 461 | 471 | 475 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:06 | 9.1 | 9 | 9.1 | 462 | 472 | 475 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:11 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:17 | 9.1 | 9.1 | 9.1 | 465 | 475 | 478 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:22 | 9.1 | 9.1 | 9.1 | 463 | 474 | 476 | 1 | 0 | 9 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:27 | 9.1 | 9.1 | 9.1 | 463 | 474 | 476 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:32 | 9.1 | 9 | 9.1 | 463 | 473 | 476 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:37 | 9.1 | 9 | 9.1 | 463 | 473 | 475 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:42 | 9.1 | 9 | 9.1 | 463 | 473 | 475 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:49 | 9.1 | 9.1 | 9.1 | 465 | 476 | 478 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:11:55 | 9.1 | 9.1 | 9.1 | 463 | 474 | 476 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:00 | 9.1 | 9.1 | 9.1 | 463 | 474 | 476 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:05 | 9.1 | 9 | 9.1 | 462 | 472 | 474 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:10 | 9 | 9 | 9 | 461 | 471 | 473 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:16 | 9.1 | 9 | 9.1 | 463 | 473 | 474 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:21 | 9.1 | 9 | 9.1 | 463 | 473 | 475 | 2 | 0 | 10 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:26 | 9.1 | 9 | 9.1 | 463 | 473 | 475 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:31 | 9.1 | 9 | 9.1 | 463 | 473 | 475 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:37 | 9.1 | 9 | 9.1 | 463 | 474 | 475 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:44 | 9.1 | 9 | 9.1 | 463 | 474 | 475 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:49 | 9.1 | 9.1 | 9.1 | 463 | 474 | 475 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:12:54 | 9.1 | 9.1 | 9.1 | 464 | 474 | 476 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:00 |  |  | 9.1 | 465 | 475 | [5 empty] | 0 |  |  |  | 0 |  | 1 |  | 0
2026-08-26T17:13:09 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:15 | 9.1 | 9.1 | 9.1 | 464 | 475 | 477 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:20 | 9.1 | 9.1 | 9.1 | 465 | 475 | 477 | 3 | 0 | 11 | 0 | 0 | 0.3 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:25 | 8.5 | 8.5 | 8.5 | 433 | 443 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:31 | 8.5 | 8.5 | 8.5 | 434 | 444 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:36 | 8.5 | 8.5 | 8.5 | 434 | 444 | 447 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:42 | 8.5 | 8.5 | 8.5 | 434 | 444 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:47 | 8.5 | 8.5 | 8.5 | 434 | 445 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:52 | 8.5 | 8.5 | 8.5 | 434 | 444 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:13:57 | 8.5 | 8.5 | 8.5 | 434 | 444 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:02 | 8.5 | 8.5 | 8.5 | 435 | 445 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:08 | 8.5 | 8.5 | 8.5 | 434 | 444 | 446 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:13 | 8.6 | 8.5 | 8.6 | 438 | 448 | 449 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:20 | 9 | 8.9 | 9 | 458 | 467 | 470 | 4 | 0 | 12 | 0 | 0 | 0.4 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:25 | 8.9 | 8.9 | 8.9 | 455 | 464 | 467 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:30 | 8.9 | 8.9 | 8.9 | 455 | 466 | 468 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:35 | 8.9 | 8.9 | 8.9 | 456 | 466 | 468 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:41 | 8.9 | 8.9 | 8.9 | 456 | 466 | 468 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:46 | 8.9 | 8.9 | 8.9 | 457 | 466 | 468 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:14:51 | 9 | 8.9 | 9 | 457 | 466 | 469 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:07 | 8.9 | 8.9 | 8.9 | 455 | 466 | 467 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:13 | 8.9 | 8.9 | 8.9 | 455 | 466 | 468 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:18 | 9 | 8.9 | 8.9 | 456 | 466 | 469 | 5 | 0 | 13 | 0 | 0 | 0.5 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:23 | 8.9 | 8.9 | 8.9 | 455 | 464 | 466 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:28 | 8.9 | 8.9 | 8.9 | 455 | 465 | 467 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:34 | 8.9 | 8.9 | 8.9 | 455 | 465 | 467 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:41 | 8.9 | 8.9 | 8.9 | 455 | 466 | 468 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:46 | 9 | 8.9 | 8.9 | 456 | 466 | 469 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:51 | 8.9 | 8.9 | 8.9 | 455 | 464 | 467 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:15:56 | 9 | 8.9 | 9 | 456 | 466 | 469 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:01 | 8.9 | 8.9 | 8.9 | 455 | 465 | 467 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:08 | 8.9 | 8.9 | 8.9 | 455 | 465 | 467 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:13 | 8.9 | 8.9 | 8.9 | 455 | 465 | 468 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:18 | 8.9 | 8.9 | 8.9 | 456 | 466 | 469 | 6 | 0 | 14 | 0 | 0 | 0.6 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:23 | 8.9 | 8.9 | 8.9 | 456 | 465 | 468 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:28 | 8.9 | 8.9 | 8.9 | 456 | 466 | 468 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:34 | 8.9 | 8.9 | 8.9 | 455 | 465 | 468 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:39 | 8.9 | 8.9 | 8.9 | 455 | 466 | 468 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:44 | 8.9 | 8.9 | 8.9 | 455 | 464 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:49 | 8.9 | 8.9 | 8.9 | 455 | 464 | 466 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:16:54 | 8.9 | 8.8 | 8.8 | 455 | 464 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:00 | 8.9 | 8.8 | 8.8 | 455 | 465 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:05 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:10 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:15 | 8.9 | 8.8 | 8.8 | 454 | 464 | 467 | 7 | 0 | 15 | 0 | 0 | 0.7 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:20 | 8.9 | 8.8 | 8.8 | 454 | 465 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:26 | 8.9 | 8.8 | 8.8 | 454 | 465 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:31 | 8.9 | 8.8 | 8.9 | 455 | 465 | 468 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:36 | 8.9 | 8.8 | 8.9 | 454 | 464 | 468 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:41 | 8.9 | 8.8 | 8.9 | 454 | 464 | 468 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:46 | 8.9 | 8.8 | 8.9 | 454 | 464 | 468 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:51 | 8.9 | 8.8 | 8.8 | 454 | 464 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:17:57 | 8.9 | 8.8 | 8.9 | 454 | 464 | 468 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:02 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:07 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:12 | 8.9 | 8.8 | 8.8 | 455 | 464 | 466 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:17 | 8.9 | 8.8 | 8.9 | 455 | 464 | 467 | 8 | 0 | 16 | 0 | 0 | 0.8 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:23 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:28 | 8.9 | 8.8 | 8.9 | 455 | 464 | 468 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:33 | 8.9 | 8.8 | 8.9 | 456 | 466 | 469 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:38 | 8.9 | 8.8 | 8.9 | 456 | 466 | 468 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:43 | 8.9 | 8.8 | 8.9 | 455 | 464 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:49 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:54 | 8.9 | 8.8 | 8.9 | 454 | 464 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:18:59 | 8.9 | 8.8 | 8.9 | 455 | 465 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:04 | 8.9 | 8.8 | 8.9 | 455 | 464 | 467 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:09 | 8.9 | 8.8 | 8.9 | 455 | 464 | 466 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:15 | 8.9 | 8.8 | 8.9 | 455 | 464 | 466 | 9 | 0 | 17 | 0 | 0 | 0.9 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:20 | 8.9 | 8.8 | 8.9 | 455 | 464 | 466 | 10 | 0 | 18 | 0 | 0 | 1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:25 | 8.9 | 8.8 | 8.9 | 455 | 464 | 466 | 10 | 0 | 18 | 0 | 0 | 1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:30 | 8.9 | 8.8 | 8.8 | 454 | 464 | 466 | 10 | 0 | 18 | 0 | 0 | 1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:35 | 8.8 | 8.8 | 8.8 | 454 | 464 | 466 | 10 | 0 | 18 | 0 | 0 | 1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:19:41 | 8.8 | 8.8 | 8.8 | 455 | 464 | 467 | 10 | 0 | 18 | 0 | 0 | 1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:21:57 | 0 | 0 | 0 | 441 | 446 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:02 | 8.9 | 8.8 | 8.9 | 456 | 455 | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:07 | 8.9 | 8.8 | 8.9 | 457 | 456 | 458 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:12 | 8.9 | 8.9 | 8.9 | 458 | 457 | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:18 | 9 | 8.9 | 9 | 461 | 461 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:23 | 8.9 | 8.9 | 8.9 | 461 | 460 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:28 | 9 | 8.9 | 9 | 462 | 461 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:33 | 8.7 | 8.7 | 8.7 | 451 | 449 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:38 | 8.8 | 8.7 | 8.7 | 451 | 450 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:43 | 8.9 | 8.9 | 8.9 | 461 | 460 | 461 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:49 | 8.9 | 8.9 | 8.9 | 461 | 459 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:54 | 9 | 8.9 | 9 | 462 | 461 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:22:59 | 8.9 | 8.9 | 8.9 | 461 | 459 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:04 | 8.9 | 8.9 | 8.9 | 460 | 458 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:11 | 8.9 | 8.8 | 8.9 | 457 | 455 | 457 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:17 | 8.9 | 8.9 | 8.9 | 458 | 457 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:22 | 8.9 | 8.8 | 8.9 | 458 | 457 | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:27 | 8.9 | 8.8 | 8.9 | 457 | 456 | 459 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:32 | 8.9 | 8.8 | 8.9 | 457 | 457 | 459 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:39 | 8.9 | 8.8 | 8.9 | 458 | 457 | 459 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:44 | 8.9 | 8.8 | 8.9 | 457 | 457 | 459 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:50 | 8.9 | 8.8 | 8.9 | 457 | 457 | 459 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:23:55 | 8.9 | 8.8 | 8.9 | 457 | 456 | 458 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:00 | 8.9 | 8.8 | 8.8 | 456 | 455 | 457 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:06 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:11 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:16 | 8.9 | 8.8 | 8.9 | 456 | 455 | 458 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:22 | 8.9 | 8.8 | 8.8 | 455 | 455 | 458 | 1 | 0 | 1 | 0 | 0 | 0.1 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:27 | 8.9 | 8.8 | 8.8 | 456 | 455 | 458 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:33 | 8.9 | 8.8 | 8.9 | 456 | 455 | 458 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:38 | 8.9 | 8.8 | 8.9 | 456 | 455 | 458 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:43 | 8.9 | 8.8 | 8.9 | 456 | 455 | 458 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:48 | 8.9 | 8.8 | 8.9 | 455 | 455 | 458 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:53 | 8.8 | 8.8 | 8.8 | 455 | 454 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:24:59 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:04 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:09 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:14 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:19 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:25 | 8.8 | 8.8 | 8.8 | 454 | 453 | 455 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:31 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:37 | 8.9 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:42 | 8.9 | 8.8 | 8.8 | 456 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:47 | 8.9 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:53 | 8.9 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.1 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:25:58 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:03 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:08 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:13 | 8.8 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:21 | 8.9 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 0 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:27 | 8.9 | 8.8 | 8.8 | 455 | 455 | 457 | 2 | 1 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:33 | 8.9 | 8.8 | 8.9 | 456 | 456 | 458 | 2 | 1 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:38 | 8.9 | 8.8 | 8.9 | 456 | 457 | 458 | 2 | 1 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:43 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.7 | 0.2 | 18 | 40 | 0 | 1 | 1 | 0 | 0
2026-08-26T17:26:50 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:26:56 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:01 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:06 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:11 | 8.9 | 8.8 | 8.9 | 457 | 457 | 459 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:16 | 8.9 | 8.8 | 8.9 | 456 | 457 | 459 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:21 | 8.9 | 8.8 | 8.9 | 457 | 457 | 458 | 2 | 1 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:27 | 8.9 | 8.8 | 8.9 | 457 | 457 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:33 | 8.9 | 8.9 | 8.9 | 457 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:38 | 8.9 | 8.9 | 8.9 | 457 | 457 | 458 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:43 | 8.9 | 8.9 | 8.9 | 457 | 457 | 458 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:48 | 8.9 | 8.9 | 8.9 | 458 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:27:54 | 8.9 | 8.9 | 8.9 | 457 | 457 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:00 | 8.9 | 8.9 | 8.9 | 457 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:05 | 8.9 | 8.9 | 8.9 | 458 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:10 | 8.9 | 8.9 | 8.9 | 458 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:16 | 8.9 | 8.9 | 8.9 | 458 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:22 | 8.9 | 8.9 | 8.9 | 458 | 458 | 459 | 2 | 2 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:27 | 8.9 | 8.9 | 8.9 | 457 | 457 | 459 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:32 | 8.9 | 8.9 | 8.9 | 457 | 457 | 459 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:37 | 8.9 | 8.9 | 8.9 | 457 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:43 | 8.9 | 8.9 | 8.9 | 458 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:48 | 8.9 | 8.9 | 8.9 | 458 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:53 | 8.9 | 8.9 | 8.9 | 458 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:28:58 | 8.9 | 8.9 | 8.9 | 457 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:29:04 | 8.9 | 8.9 | 8.9 | 458 | 458 | 460 | 2 | 3 | 2 | 0 | 0.5 | 0.7 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:33:45 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 1 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:33:50 | 8.8 | 8.8 | 8.8 | 450 | 451 | 453 | 0 | 1 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:33:55 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 1 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:01 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 1 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:06 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:11 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:16 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:21 | 8.8 | 8.8 | 8.8 | 450 | 451 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:27 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:32 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:34:39 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:34:44 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:34:49 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:34:55 | 8.8 | 8.8 | 8.8 | 451 | 450 | 453 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:35:03 | 8.8 | 8.8 | 8.8 | 451 | 450 | 453 | 0 | 2 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:08 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 3 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:13 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 3 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:19 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 3 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:24 | 8.8 | 8.8 | 8.8 | 450 | 451 | 453 | 0 | 3 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:29 | 8.8 | 8.8 | 8.8 | 450 | 449 | 453 | 0 | 3 | 0 | 0 | 1.5 | 0.1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:37 | 8.8 | 8.7 | 8.8 | 449 | 449 | 452 | 0 | 3 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:43 | 8.8 | 8.7 | 8.8 | 449 | 449 | 451 | 0 | 3 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:48 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 3 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:53 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 3 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:35:59 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 3 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:04 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:10 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:15 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:20 | 8.8 | 8.7 | 8.8 | 450 | 450 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:25 | 8.8 | 8.7 | 8.8 | 449 | 450 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:30 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:36 | 8.8 | 8.8 | 8.8 | 450 | 451 | 452 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:41 | 8.8 | 8.7 | 8.8 | 449 | 451 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:46 | 8.8 | 8.7 | 8.8 | 449 | 450 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:51 | 8.8 | 8.7 | 8.8 | 450 | 450 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:36:56 | 8.8 | 8.7 | 8.8 | 449 | 449 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:37:01 | 8.8 | 8.7 | 8.8 | 450 | 450 | 451 | 0 | 4 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:37:07 | 8.8 | 8.7 | 8.8 | 450 | 450 | 451 | 0 | 5 | 0 | 0 | 15 | 1 | 180 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:45:44 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 13 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:45:50 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 13 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:45:55 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:00 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:06 | 8.9 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:11 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:15 | 8.9 | 8.8 | 8.9 | 451 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:20 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:25 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:30 | 8.9 | 8.8 | 8.9 | 453 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:35 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:41 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:47 | 8.9 | 8.8 | 8.9 | 452 | 452 | 453 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 1.8 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:52 | 8.9 | 8.8 | 8.9 | 453 | 453 | 454 | 0 | 14 | 0 | 0 | 15 | 1 | 18 | 18 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:46:58 | 8.8 | 8.8 | 8.8 | 452 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 18 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:07 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:12 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:17 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:22 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:28 | 8.8 | 8.8 | 8.8 | 451 | 450 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:33 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:38 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:43 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:48 | 8.8 | 8.8 | 8.8 | 451 | 451 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:53 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:47:59 | 8.8 | 8.8 | 8.8 | 450 | 451 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:04 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:09 | 8.8 | 8.8 | 8.8 | 450 | 450 | 452 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:14 | 8.8 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:19 | 8.9 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:26 | 8.9 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:31 | 8.9 | 8.8 | 8.9 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:36 | 8.9 | 8.8 | 8.8 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:41 | 8.9 | 8.8 | 8.9 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:48 | 8.9 | 8.8 | 8.9 | 451 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:53 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:48:58 | 8.9 | 8.8 | 8.9 | 452 | 451 | 453 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:49:04 | 8.9 | 8.8 | 8.9 | 452 | 452 | 454 | 0 | 15 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:49:09 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 1 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:49:14 | 8.9 | 8.8 | 8.9 | 451 | 451 | 453 | 0 | 1 | 0 | 0 | 15 | 1 | 18 | 180 | 400 | 1 | 1 | 0 | 0
2026-08-26T17:52:00 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 3 | 0 | 18 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:06 | 8.9 | 8.8 | 8.9 | 453 | 451 | 455 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:11 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:16 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:22 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:27 | 8.9 | 8.8 | 8.9 | 451 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:32 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:37 | 8.9 | 8.8 | 8.9 | 452 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:42 | 8.9 | 8.8 | 8.9 | 452 | 451 | 453 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:48 | 8.9 | 8.8 | 8.9 | 453 | 451 | 453 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:53 | 8.9 | 8.8 | 8.9 | 453 | 451 | 454 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:52:58 | 8.9 | 8.8 | 8.9 | 452 | 451 | 453 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:03 | 8.9 | 8.8 | 8.9 | 453 | 451 | 453 | 0 | 4 | 0 | 19 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:08 | 8.9 | 8.8 | 8.9 | 453 | 451 | 453 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:13 | 8.9 | 8.8 | 8.9 | 453 | 452 | 454 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:19 | 8.9 | 8.8 | 8.9 | 453 | 453 | 455 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:24 | 8.9 | 8.9 | 8.9 | 453 | 452 | 455 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:29 | 8.9 | 8.9 | 8.9 | 453 | 452 | 455 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:34 | 8.9 | 8.9 | 8.9 | 453 | 452 | 455 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:39 | 8.9 | 8.9 | 8.9 | 453 | 452 | 455 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:45 | 8.9 | 8.9 | 8.9 | 453 | 452 | 454 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:50 | 8.9 | 8.8 | 8.9 | 453 | 452 | 454 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:53:55 | 8.9 | 8.8 | 8.9 | 453 | 452 | 454 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:54:00 | 8.9 | 8.9 | 8.9 | 453 | 452 | 454 | 0 | 5 | 0 | 20 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:54:05 | 8.9 | 8.9 | 8.9 | 453 | 453 | 455 | 0 | 6 | 0 | 21 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:54:10 | 8.9 | 8.9 | 8.9 | 453 | 453 | 455 | 0 | 6 | 0 | 21 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-26T17:54:16 | 8.9 | 8.9 | 8.9 | 453 | 453 | 455 | 0 | 6 | 0 | 21 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:19:59 |  |  | 0 | 0 | 0 | [6 empty] | 1 | [5 empty] | 0 | 2
2026-08-27T12:20:09 |  |  | 0 | 0 | 0 | [6 empty] | 1 | [5 empty] | 0 | 2
2026-08-27T12:20:16 |  |  | 0 | 0 | 0 | [6 empty] | 1 | [5 empty] | 0 | 2
2026-08-27T12:20:24 |  |  | 0 | 0 | 0 | [6 empty] | 1 | [5 empty] | 0 | 2
2026-08-27T12:20:31 |  |  | 0 | 427 | 433 | [6 empty] | 1 | [5 empty] | 174 | 2
2026-08-27T12:20:40 |  |  | 7.8 | 438 | 438 | [6 empty] | 1 | [5 empty] | 184 | 2
2026-08-27T12:20:48 |  |  | 7.8 | 438 | 438 | [6 empty] | 1 | [5 empty] | 184 | 2
2026-08-27T12:20:55 |  |  | 7.8 | 439 | 439 | [6 empty] | 1 | [5 empty] | 184 | 2
2026-08-27T12:21:05 |  |  | 7.8 | 439 | 439 | [6 empty] | 1 | [5 empty] | 184 | 2
2026-08-27T12:21:14 |  |  | 7.8 | 439 | 439 | [6 empty] | 1 | [5 empty] | 184 | 2
2026-08-27T12:21:40 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:21:45 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:21:50 | 7.8 | 7.8 | 7.8 | 439 | 439 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:21:55 | 7.8 | 7.8 | 7.8 | 439 | 439 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:00 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:05 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:11 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:16 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:21 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:26 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 1 | 0 | 22 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:31 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:37 | 7.8 | 7.8 | 7.8 | 439 | 438 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:42 | 7.9 | 7.8 | 7.8 | 440 | 439 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:47 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:22:53 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:23:04 |  |  | 2 | 438 | [7 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T12:23:44 | 2 | 2 | 2 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:23:50 | 2 | 2 | 2 | 437 | 436 | 439 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:23:55 | 2 | 2 | 2 | 437 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:00 | 2 | 2 | 2 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:06 | 2 | 2 | 2 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:12 | 2 | 2 | 2 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:18 | 2 | 2 | 2 | 438 | 437 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:23 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:28 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:33 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:38 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:44 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:49 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:54 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:24:59 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:04 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:11 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:16 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:21 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:27 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:33 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:39 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:45 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:50 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:25:55 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:00 | 7.8 | 7.8 | 7.8 | 438 | 439 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:06 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:12 | 7.8 | 7.8 | 7.8 | 439 | 439 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:17 | 7.8 | 7.8 | 7.8 | 439 | 439 | 440 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:23 | 7.8 | 7.8 | 7.8 | 439 | 439 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:28 | 7.8 | 7.8 | 7.8 | 438 | 439 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:33 | 7.8 | 7.8 | 7.8 | 438 | 439 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:39 | 7.8 | 7.8 | 7.8 | 438 | 438 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:44 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:49 | 7.8 | 7.8 | 7.8 | 436 | 436 | 439 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:54 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:26:59 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:04 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:10 | 7.8 | 7.8 | 7.8 | 438 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:15 | 7.8 | 7.8 | 7.8 | 438 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:20 | 7.8 | 7.8 | 7.8 | 438 | 438 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:25 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:30 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:36 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:41 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:46 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:51 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:27:56 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:01 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:07 | 7.8 | 7.8 | 7.8 | 438 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:12 | 7.8 | 7.8 | 7.8 | 439 | 439 | 441 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:17 | 7.8 | 7.8 | 7.8 | 439 | 438 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:22 | 7.8 | 7.8 | 7.8 | 438 | 438 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:27 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:33 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:38 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 2 | 0 | 23 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:43 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:48 | 7.8 | 7.8 | 7.8 | 439 | 440 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:53 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:28:58 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:04 | 7.8 | 7.8 | 7.8 | 438 | 438 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:09 | 7.8 | 7.8 | 7.8 | 439 | 439 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:15 | 7.8 | 7.8 | 7.8 | 439 | 439 | 441 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:20 | 7.8 | 7.8 | 7.8 | 439 | 439 | 441 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:25 | 7.8 | 7.8 | 7.8 | 440 | 439 | 441 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:30 | 7.8 | 7.8 | 7.8 | 437 | 438 | 440 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:36 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 1 | 0 | 24 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:42 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:47 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:52 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:29:58 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:03 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:08 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:13 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:18 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:23 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:29 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:34 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:39 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 2 | 0 | 25 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:44 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:49 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:30:54 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:00 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:05 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:10 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:15 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:20 | 7.8 | 7.8 | 7.8 | 440 | 439 | 441 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:26 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:32 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:37 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 3 | 0 | 26 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:42 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:47 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:52 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:31:58 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:03 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:08 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:13 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:18 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:23 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:29 | 7.8 | 7.8 | 7.8 | 441 | 441 | 443 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:34 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 4 | 0 | 27 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:39 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:44 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:49 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:32:55 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:00 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:05 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:10 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:15 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:21 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:28 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:34 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 5 | 0 | 28 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:39 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:44 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:51 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:33:56 | 7.8 | 7.8 | 7.8 | 440 | 439 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:01 | 7.8 | 7.8 | 7.8 | 440 | 439 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:06 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:11 | 7.8 | 7.8 | 7.8 | 440 | 439 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:16 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:23 | 7.8 | 7.8 | 7.8 | 440 | 439 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:28 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:33 | 7.8 | 7.8 | 7.8 | 440 | 440 | 443 | 0 | 6 | 0 | 29 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:38 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:43 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:48 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:54 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:34:59 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:04 | 7.8 | 7.8 | 7.8 | 441 | 439 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:09 | 7.8 | 7.8 | 7.8 | 439 | 437 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:14 | 7.8 | 7.8 | 7.8 | 438 | 437 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:20 | 7.8 | 7.8 | 7.8 | 438 | 437 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:25 | 7.8 | 7.8 | 7.8 | 438 | 438 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:30 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:35 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:40 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:45 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:51 | 7.8 | 7.8 | 7.8 | 440 | 439 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:35:56 | 7.8 | 7.8 | 7.8 | 441 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:01 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:06 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:12 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:17 | 7.8 | 7.8 | 7.8 | 441 | 440 | 444 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:23 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:28 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:34 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:39 | 7.8 | 7.8 | 7.8 | 439 | 438 | 440 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:44 | 7.8 | 7.8 | 7.8 | 441 | 439 | 442 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:49 | 7.8 | 7.8 | 7.8 | 442 | 440 | 444 | 0 | 7 | 0 | 30 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:36:54 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:00 | 7.8 | 7.8 | 7.8 | 441 | 440 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:05 | 7.8 | 7.8 | 7.8 | 442 | 440 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:10 | 7.8 | 7.8 | 7.8 | 442 | 440 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:15 | 7.9 | 7.8 | 7.9 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:20 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:25 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:32 | 7.9 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:38 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:43 | 7.9 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:48 | 7.8 | 7.8 | 7.8 | 441 | 441 | 444 | 0 | 1 | 0 | 31 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:53 | 7.9 | 7.8 | 7.9 | 442 | 442 | 445 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:37:58 | 7.9 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:04 | 7.9 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:09 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:14 | 7.8 | 7.8 | 7.8 | 441 | 441 | 443 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:19 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:24 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:30 | 7.8 | 7.8 | 7.8 | 441 | 441 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:35 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:40 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:45 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 2 | 0 | 32 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:50 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:38:55 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:01 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:06 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:11 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:16 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:21 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:27 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:34 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:39 | 7.8 | 7.8 | 7.8 | 442 | 440 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:44 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 3 | 0 | 33 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:49 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:39:54 | 7.8 | 7.8 | 7.8 | 441 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:00 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:05 | 7.8 | 7.8 | 7.8 | 442 | 440 | 444 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:10 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:15 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:20 | 7.8 | 7.8 | 7.8 | 442 | 441 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:25 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:31 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:36 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:41 | 7.8 | 7.8 | 7.8 | 442 | 441 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:46 | 7.8 | 7.8 | 7.8 | 442 | 441 | 443 | 0 | 4 | 0 | 34 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:51 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:40:57 | 7.8 | 7.8 | 7.8 | 440 | 439 | 441 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:02 | 7.8 | 7.8 | 7.8 | 443 | 442 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:08 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:13 | 7.9 | 7.8 | 7.8 | 443 | 441 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:18 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:24 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:29 | 7.8 | 7.8 | 7.8 | 442 | 440 | 443 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:34 | 7.9 | 7.8 | 7.9 | 443 | 441 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:39 | 7.9 | 7.8 | 7.8 | 443 | 441 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:44 | 7.9 | 7.8 | 7.8 | 443 | 442 | 444 | 0 | 5 | 0 | 35 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:49 | 7.8 | 7.8 | 7.8 | 440 | 438 | 441 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:41:55 | 7.9 | 7.8 | 7.9 | 442 | 442 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:00 | 7.9 | 7.8 | 7.9 | 443 | 442 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:05 | 7.9 | 7.8 | 7.9 | 442 | 442 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:10 | 7.9 | 7.8 | 7.9 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:15 | 7.9 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:20 | 7.9 | 7.8 | 7.9 | 443 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:26 | 7.9 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:31 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:36 | 7.8 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:43 | 7.9 | 7.8 | 7.8 | 442 | 441 | 444 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:48 | 7.9 | 7.8 | 7.9 | 442 | 441 | 444 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:53 | 7.9 | 7.8 | 7.9 | 442 | 441 | 445 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:42:58 | 7.9 | 7.9 | 7.9 | 444 | 442 | 445 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:04 | 7.9 | 7.9 | 7.9 | 443 | 442 | 445 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:09 | 7.9 | 7.9 | 7.9 | 443 | 442 | 445 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:14 | 7.8 | 7.8 | 7.8 | 440 | 440 | 442 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:19 | 24.8 | 24.8 | 24.8 | 440 | 440 | 443 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:24 | 24.8 | 24.7 | 24.8 | 440 | 439 | 442 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:29 | 24.8 | 24.7 | 24.8 | 440 | 439 | 442 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:35 | 24.7 | 24.7 | 24.7 | 440 | 439 | 442 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:40 | 24.7 | 24.6 | 24.7 | 440 | 439 | 442 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:45 | 24.7 | 24.6 | 24.7 | 443 | 442 | 445 | 0 | 7 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:43:50 |  |  | 7.8 | 0 | 0 | [6 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T12:44:05 | 7.8 | 7.8 | 7.8 | 444 | 442 | 445 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:10 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:15 | 7.8 | 7.8 | 7.8 | 444 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:20 | 7.8 | 7.8 | 7.8 | 443 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:26 | 7.8 | 7.8 | 7.8 | 444 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:33 | 7.8 | 7.8 | 7.8 | 443 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:38 | 7.8 | 7.8 | 7.8 | 443 | 487 | 490 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:43 | 7.8 | 7.8 | 7.8 | 443 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:48 | 7.8 | 7.8 | 7.8 | 443 | 488 | 490 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:53 | 7.8 | 7.8 | 7.8 | 443 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:44:59 | 7.8 | 7.8 | 7.8 | 442 | 487 | 490 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:04 | 7.8 | 7.8 | 7.8 | 443 | 487 | 490 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:09 | 7.8 | 7.8 | 7.8 | 442 | 487 | 490 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:14 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:19 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:24 | 7.8 | 7.8 | 7.8 | 442 | 487 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:30 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:35 | 7.8 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:40 | 7.8 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:45 | 7.8 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:50 | 7.8 | 7.7 | 7.8 | 439 | 484 | 489 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:45:55 | 7.8 | 7.8 | 7.8 | 440 | 485 | 489 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:01 | 7.8 | 7.7 | 7.8 | 440 | 485 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:06 | 7.8 | 7.8 | 7.8 | 440 | 485 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:11 | 7.8 | 7.8 | 7.8 | 440 | 485 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:16 | 7.8 | 7.8 | 7.8 | 440 | 484 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:22 | 7.8 | 7.8 | 7.8 | 440 | 484 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:28 | 7.8 | 7.8 | 7.8 | 440 | 484 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:33 | 7.8 | 7.8 | 7.8 | 440 | 485 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:38 | 7.8 | 7.8 | 7.8 | 440 | 485 | 488 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:43 | 7.8 | 7.8 | 7.8 | 443 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:48 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:46:54 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:00 | 7.8 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:05 | 7.8 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:10 | 7.8 | 7.8 | 7.8 | 444 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:15 | 7.8 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:21 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:27 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:32 | 7.8 | 7.8 | 7.8 | 441 | 486 | 489 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:37 | 7.8 | 7.8 | 7.8 | 441 | 486 | 489 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:42 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:48 | 7.8 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:54 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:47:59 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:04 | 7.8 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:09 | 7.8 | 7.8 | 7.8 | 444 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:14 | 7.8 | 7.8 | 7.8 | 444 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:19 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:25 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:30 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:35 | 7.8 | 7.8 | 7.8 | 444 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:40 | 7.8 | 7.8 | 7.8 | 444 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:45 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:50 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:48:56 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:01 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:06 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:11 | 7.8 | 7.8 | 7.8 | 444 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:16 | 7.8 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:22 | 7.8 | 7.8 | 7.8 | 443 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:27 | 7.8 | 7.8 | 7.8 | 443 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:32 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:37 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:42 | 7.8 | 7.8 | 7.8 | 443 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:47 | 7.8 | 7.8 | 7.8 | 443 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:53 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:49:58 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:03 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:08 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:14 | 7.8 | 7.8 | 7.8 | 442 | 487 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:19 | 7.8 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:25 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:30 | 7.9 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:35 | 7.9 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:40 | 7.8 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:45 | 7.9 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:50 | 7.9 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:50:56 | 7.9 | 7.8 | 7.8 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:01 | 7.9 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:06 | 7.9 | 7.8 | 7.8 | 443 | 489 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:11 | 7.9 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:16 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:22 | 7.9 | 7.8 | 7.8 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:27 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0
2026-08-27T12:51:33 | 7.9 | 7.8 | 7.9 | 443 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:51:38 | 7.9 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:51:44 | 7.9 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:51:49 | 7.9 | 7.8 | 7.8 | 442 | 488 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:51:54 | 7.9 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:51:59 | 7.9 | 7.8 | 7.8 | 442 | 488 | 491 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:04 | 7.9 | 7.8 | 7.9 | 442 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:09 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:15 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:20 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:25 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:30 | 7.9 | 7.8 | 7.9 | 443 | 489 | 493 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:35 | 7.9 | 7.9 | 7.9 | 444 | 489 | 493 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:40 | 7.9 | 7.9 | 7.9 | 444 | 489 | 493 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:46 | 7.9 | 7.8 | 7.9 | 443 | 489 | 492 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:51 | 7.9 | 7.9 | 7.9 | 444 | 489 | 493 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:52:56 | 7.9 | 7.9 | 7.9 | 444 | 489 | 493 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:53:01 | 7.9 | 7.9 | 7.9 | 444 | 442 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T12:53:06 | 7.9 | 7.9 | 7.9 | 444 | 442 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:11 | 7.9 | 7.9 | 7.9 | 444 | 443 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:17 | 7.9 | 7.9 | 7.9 | 444 | 443 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:22 | 7.9 | 7.9 | 7.9 | 445 | 443 | 447 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:27 | 7.9 | 7.9 | 7.9 | 444 | 443 | 447 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:32 | 7.9 | 7.9 | 7.9 | 444 | 443 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:37 | 7.9 | 7.9 | 7.9 | 444 | 442 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:43 | 7.9 | 7.9 | 7.9 | 445 | 443 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:48 | 7.9 | 7.9 | 7.9 | 445 | 444 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:53 | 7.9 | 7.9 | 7.9 | 445 | 444 | 446 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:53:58 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 6 | 0 | 36 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:03 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:08 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:14 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:20 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:25 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:30 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:35 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:41 | 7.9 | 7.9 | 7.9 | 445 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:46 | 7.9 | 7.9 | 7.9 | 446 | 444 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:51 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:54:56 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 1 | 0 | 37 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:01 | 7.9 | 7.9 | 7.9 | 445 | 444 | 448 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:06 | 7.9 | 7.9 | 7.9 | 445 | 445 | 448 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:12 | 7.9 | 7.9 | 7.9 | 445 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:17 | 7.9 | 7.9 | 7.9 | 445 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:22 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:27 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:32 | 7.9 | 7.9 | 7.9 | 447 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:38 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:44 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:49 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:54 | 7.9 | 7.9 | 7.9 | 446 | 445 | 447 | 0 | 2 | 0 | 38 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:55:59 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:05 | 7.9 | 7.9 | 7.9 | 447 | 446 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:11 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:16 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:21 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:26 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:31 | 7.9 | 7.9 | 7.9 | 446 | 445 | 448 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:39 | 7.9 | 7.9 | 7.9 | 447 | 445 | 449 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:45 | 7.9 | 7.9 | 7.9 | 447 | 446 | 449 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:50 | 7.9 | 7.9 | 7.9 | 447 | 447 | 449 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:56:55 | 7.9 | 7.9 | 7.9 | 447 | 447 | 449 | 0 | 3 | 0 | 39 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:00 | 7.9 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:06 | 7.9 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:11 | 8 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:16 | 8 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:21 | 8 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:26 | 8 | 7.9 | 8 | 448 | 448 | 451 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:34 | 8 | 7.9 | 8 | 448 | 447 | 451 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:39 | 8 | 7.9 | 7.9 | 447 | 447 | 450 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:44 | 8 | 7.9 | 8 | 449 | 447 | 451 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:49 | 8 | 7.9 | 7.9 | 448 | 447 | 451 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:54 | 8 | 7.9 | 8 | 448 | 447 | 451 | 0 | 4 | 0 | 40 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:57:59 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:05 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:10 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:15 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:20 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:25 | 8 | 7.9 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:30 | 8 | 7.9 | 8 | 449 | 449 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:36 | 8 | 8 | 8 | 449 | 448 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:41 | 8 | 8 | 8 | 449 | 449 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:46 | 8 | 8 | 8 | 450 | 449 | 451 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:51 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:58:56 | 8 | 8 | 8 | 449 | 449 | 452 | 0 | 5 | 0 | 41 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:01 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:07 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:12 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:17 | 8 | 8 | 8 | 450 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:22 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:27 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:33 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:38 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:43 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:48 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:53 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 6 | 0 | 42 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T12:59:58 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:04 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:09 | 8 | 8 | 8 | 450 | 449 | 452 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:14 | 8 | 8 | 8 | 451 | 450 | 453 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:19 | 8 | 8 | 8 | 451 | 449 | 453 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:24 | 8 | 8 | 8 | 451 | 449 | 453 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:30 | 8 | 8 | 8 | 451 | 449 | 453 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:00:35 | 7.9 | 7.8 | 7.9 | 319 | 430 | 433 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:00:40 | 7.9 | 7.8 | 7.8 | 509 | 521 | 523 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:00:45 | 7.9 | 7.8 | 7.9 | 535 | 458 | 461 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:00:50 | 7.9 | 7.8 | 7.9 | 534 | 430 | 432 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:00:55 | 7.9 | 7.8 | 7.8 | 533 | 429 | 432 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:01:01 | 7.8 | 7.8 | 7.8 | 440 | 379 | 382 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:07 | 7.7 | 7.7 | 7.7 | 303 | 272 | 376 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:12 | 7.7 | 7.7 | 7.7 | 191 | 184 | 376 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:01:17 | 7.7 | 7.7 | 7.7 | 327 | 312 | 327 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:01:23 | 7.7 | 7.7 | 7.7 | 314 | 312 | 314 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:01:28 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:33 | 7.7 | 7.7 | 7.7 | 435 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:38 | 7.7 | 7.7 | 7.7 | 434 | 433 | 435 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:43 | 7.7 | 7.7 | 7.7 | 434 | 433 | 435 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:49 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:01:54 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:01 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:06 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:11 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:16 | 7.7 | 7.7 | 7.7 | 434 | 432 | 435 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:21 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 7 | 0 | 43 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:02:26 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:32 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:37 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:42 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:47 | 7.7 | 7.7 | 7.7 | 434 | 432 | 435 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:52 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:02:58 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:03:03 | 7.7 | 7.7 | 7.7 | 434 | 432 | 435 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:03:08 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:03:13 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 1 | 0 | 44 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:04:47 | 7.7 | 7.7 | 7.7 | 435 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:04:52 | 7.7 | 7.7 | 7.7 | 435 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:04:58 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:03 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:08 | 7.7 | 7.7 | 7.7 | 434 | 434 | 437 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:13 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:18 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:24 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:29 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:34 | 7.7 | 7.7 | 7.7 | 435 | 434 | 436 | 0 | 1 | 0 | 45 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:39 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:44 | 7.7 | 7.7 | 7.7 | 435 | 433 | 437 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:49 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:05:55 | 7.7 | 7.7 | 7.7 | 434 | 434 | 437 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:00 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:06 | 7.7 | 7.7 | 7.7 | 435 | 435 | 437 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:12 | 7.7 | 7.7 | 7.7 | 436 | 435 | 438 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:17 | 7.7 | 7.7 | 7.7 | 435 | 434 | 438 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:22 | 7.7 | 7.7 | 7.7 | 435 | 434 | 438 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:28 | 7.7 | 7.7 | 7.7 | 435 | 434 | 438 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:33 | 7.7 | 7.7 | 7.7 | 436 | 434 | 438 | 0 | 2 | 0 | 46 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:39 | 7.7 | 7.7 | 7.7 | 436 | 434 | 438 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:44 | 7.7 | 7.7 | 7.7 | 436 | 434 | 437 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:49 | 7.7 | 7.7 | 7.7 | 436 | 434 | 438 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:06:55 | 7.7 | 7.7 | 7.7 | 436 | 435 | 438 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:00 | 7.7 | 7.7 | 7.7 | 436 | 434 | 438 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:05 | 7.7 | 7.7 | 7.7 | 436 | 434 | 438 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:10 | 7.7 | 7.7 | 7.7 | 435 | 435 | 437 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:15 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:20 | 7.7 | 7.7 | 7.7 | 436 | 434 | 436 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:26 | 7.7 | 7.7 | 7.7 | 435 | 434 | 436 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:31 | 7.7 | 7.7 | 7.7 | 436 | 434 | 436 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:07:35 | 7.7 | 7.7 | 7.7 | 435 | 434 | 436 | 0 | 3 | 0 | 47 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:04 | 7.7 | 7.7 | 7.7 | 434 | 434 | 436 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:09 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:14 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:19 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:24 | 7.7 | 7.7 | 7.7 | 435 | 434 | 437 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:29 | 7.7 | 7.7 | 7.7 | 434 | 434 | 437 | 0 | 5 | 0 | 49 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:35 | 7.7 | 7.7 | 7.7 | 434 | 433 | 437 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:40 | 7.7 | 7.7 | 7.7 | 434 | 434 | 437 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:45 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:50 | 7.7 | 7.7 | 7.7 | 434 | 433 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:09:55 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:01 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:07 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:12 | 7.7 | 7.7 | 7.7 | 433 | 431 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:17 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:22 | 7.7 | 7.7 | 7.7 | 433 | 432 | 435 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:28 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:33 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 6 | 0 | 50 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:38 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:43 | 7.7 | 7.7 | 7.7 | 434 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:48 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:53 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:10:59 | 7.7 | 7.7 | 7.7 | 432 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:04 | 7.7 | 7.7 | 7.7 | 433 | 432 | 435 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:09 | 7.7 | 7.7 | 7.7 | 433 | 432 | 436 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:14 | 7.7 | 7.7 | 7.7 | 433 | 432 | 435 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:19 | 7.7 | 7.7 | 7.7 | 432 | 432 | 435 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:24 | 7.7 | 7.7 | 7.7 | 433 | 432 | 435 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:30 | 7.7 | 7.7 | 7.7 | 432 | 431 | 434 | 0 | 7 | 0 | 51 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:35 | 7.7 | 7.7 | 7.7 | 432 | 431 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:40 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:45 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:50 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:11:56 | 7.7 | 7.6 | 7.7 | 432 | 431 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:01 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:06 | 7.7 | 7.7 | 7.7 | 432 | 431 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:11 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:16 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:21 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:27 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 8 | 0 | 52 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:32 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:38 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:43 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:48 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:53 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:12:59 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:04 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:10 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:15 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:20 | 7.7 | 7.7 | 7.7 | 432 | 433 | 435 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:27 | 7.7 | 7.7 | 7.7 | 432 | 432 | 435 | 0 | 9 | 0 | 53 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:33 | 7.7 | 7.6 | 7.7 | 432 | 433 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:38 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:43 | 7.7 | 7.7 | 7.7 | 432 | 433 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:48 | 7.7 | 7.7 | 7.7 | 432 | 433 | 435 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:54 | 7.7 | 7.7 | 7.7 | 432 | 433 | 435 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:13:59 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:04 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:09 | 7.7 | 7.7 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:14 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:19 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:25 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 10 | 0 | 54 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:30 | 7.7 | 7.6 | 7.7 | 432 | 432 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:35 | 7.7 | 7.6 | 7.7 | 432 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:40 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:45 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:50 | 7.7 | 7.6 | 7.7 | 431 | 430 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:14:56 | 7.7 | 7.6 | 7.7 | 431 | 430 | 433 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:01 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:06 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:11 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:16 | 7.7 | 7.6 | 7.7 | 431 | 431 | 433 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:21 | 7.7 | 7.6 | 7.7 | 431 | 431 | 433 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:27 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 11 | 0 | 55 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:32 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:37 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:42 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:47 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:53 | 7.7 | 7.6 | 7.7 | 431 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:15:58 | 7.7 | 7.6 | 7.6 | 431 | 430 | 433 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:05 | 7.7 | 7.6 | 7.6 | 430 | 431 | 433 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:10 | 7.7 | 7.6 | 7.7 | 430 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:16 | 7.7 | 7.6 | 7.7 | 430 | 431 | 433 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:22 | 7.7 | 7.6 | 7.7 | 430 | 431 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:27 | 7.7 | 7.6 | 7.6 | 430 | 432 | 434 | 0 | 12 | 0 | 56 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:38 | 7.7 | 7.6 | 7.7 | 430 | 431 | 434 | 0 | 13 | 0 | 57 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:43 | 7.6 | 7.6 | 7.6 | 430 | 430 | 433 | 0 | 13 | 0 | 57 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:49 | 7.7 | 7.6 | 7.6 | 430 | 430 | 433 | 0 | 13 | 0 | 57 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:16:54 | 7.7 | 7.6 | 7.6 | 430 | 431 | 433 | 0 | 13 | 0 | 57 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:17:00 | 7.6 | 7.6 | 7.6 | 430 | 430 | 433 | 0 | 13 | 0 | 57 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:20:11 | 7.6 | 7.6 | 7.6 | 429 | 429 | 430 | 0 | 15 | 0 | 59 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:20:23 | 7.6 | 7.6 | 7.6 | 429 | 429 | 430 | 0 | 15 | 0 | 59 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:20:28 | 7.6 | 7.6 | 7.6 | 429 | 429 | 430 | 0 | 15 | 0 | 59 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:20:38 | 7.6 | 7.6 | 7.6 | 429 | 429 | 430 | 0 | 15 | 0 | 59 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:20:43 | 7.6 | 7.6 | 7.6 | 429 | 429 | 430 | 0 | 1 | 0 | 60 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:21:39 | 7.6 | 7.6 | 7.6 | 428 | 428 | 430 | 0 | 1 | 0 | 60 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:21:44 | 7.6 | 7.6 | 7.6 | 427 | 427 | 430 | 0 | 2 | 0 | 61 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:28:37 | 7.6 | 7.5 | 7.6 | 427 | 427 | 429 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:28:46 | 7.6 | 7.5 | 7.6 | 427 | 427 | 429 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:28:56 | 7.6 | 7.5 | 7.6 | 427 | 427 | 429 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:07 | 7.6 | 7.5 | 7.6 | 427 | 427 | 429 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:12 | 7.6 | 7.5 | 7.6 | 427 | 427 | 428 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:17 | 7.6 | 7.5 | 7.5 | 427 | 426 | 428 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:27 | 7.6 | 7.5 | 7.5 | 426 | 426 | 427 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:32 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 9 | 0 | 68 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:37 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:42 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:47 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:54 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:29:59 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:04 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:09 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:14 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:21 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:26 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:31 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 10 | 0 | 69 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:36 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:41 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:46 | 7.5 | 7.5 | 7.5 | 425 | 424 | 426 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:52 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:30:57 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:02 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:07 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:12 | 7.5 | 7.5 | 7.5 | 425 | 423 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:29 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 11 | 0 | 70 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:38 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:53 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:31:58 | 7.5 | 7.5 | 7.5 | 425 | 424 | 427 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:04 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:10 | 7.5 | 7.5 | 7.5 | 425 | 425 | 427 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:15 | 7.5 | 7.5 | 7.5 | 424 | 424 | 426 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:20 | 7.5 | 7.5 | 7.5 | 424 | 424 | 426 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:26 | 7.5 | 7.5 | 7.5 | 424 | 424 | 426 | 0 | 12 | 0 | 71 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:31 | 7.5 | 7.5 | 7.5 | 423 | 423 | 426 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:40 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:46 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:51 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:32:56 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:03 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:08 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:13 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:18 | 7.5 | 7.5 | 7.5 | 423 | 423 | 425 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:23 | 7.5 | 7.5 | 7.5 | 422 | 422 | 424 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:29 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 13 | 0 | 72 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:34 | 7.5 | 7.5 | 7.5 | 422 | 422 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:39 | 7.5 | 7.5 | 7.5 | 421 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:44 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:49 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:33:54 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:00 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:05 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:10 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:15 | 7.5 | 7.5 | 7.5 | 422 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:21 | 7.5 | 7.5 | 7.5 | 421 | 421 | 423 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:26 | 7.5 | 7.4 | 7.5 | 421 | 421 | 422 | 0 | 14 | 0 | 73 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:34:37 | 7.5 | 7.4 | 7.5 | 421 | 421 | 421 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:34:42 | 7.5 | 7.4 | 7.5 | 421 | 421 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:34:47 | 7.5 | 7.4 | 7.5 | 421 | 421 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:34:52 | 7.5 | 7.5 | 7.5 | 421 | 422 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:34:57 | 7.5 | 7.5 | 7.5 | 421 | 422 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:07 | 7.5 | 7.5 | 7.5 | 421 | 422 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:12 | 7.5 | 7.5 | 7.5 | 422 | 423 | 424 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:18 | 7.5 | 7.5 | 7.5 | 421 | 422 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:32 | 7.5 | 7.5 | 7.5 | 421 | 422 | 424 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:42 | 7.5 | 7.5 | 7.5 | 421 | 423 | 425 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:35:48 | 7.5 | 7.5 | 7.5 | 422 | 423 | 425 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:35:53 | 7.5 | 7.5 | 7.5 | 421 | 422 | 424 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:36:03 | 7.5 | 7.5 | 7.5 | 421 | 421 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:36:08 | 7.5 | 7.4 | 7.5 | 421 | 421 | 423 | 0 | 15 | 0 | 74 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T13:40:18 | 7.5 | 7.4 | 7.5 | 420 | 420 | 421 | 0 | 1 | 0 | 75 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:40:23 | 7.5 | 7.4 | 7.4 | 420 | 419 | 421 | 0 | 1 | 0 | 75 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T13:40:28 | 7.5 | 7.4 | 7.4 | 420 | 419 | 421 | 0 | 1 | 0 | 75 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T14:39:15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:39:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T14:40:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 107 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T15:24:55 |  |  | 0 | 0 | [7 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T15:25:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:25:31 |  |  | 0 | 0 | 0 | [6 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T15:25:44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:25:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:10 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:16 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:21 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:27 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:32 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:37 | 0 | 0 | 0 | 433 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:43 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:50 | 0 | 0 | 0 | 432 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:26:55 | 0 | 0 | 0 | 433 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:05 | 0 | 0 | 0 | 435 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:11 | 0 | 0 | 0 | 435 | 434 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:27:57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:28:56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:17 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:22 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:27 | 0 | 0 | 0 | 436 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:32 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:37 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:43 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:48 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:53 | 0 | 0 | 0 | 436 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:29:58 | 0 | 0 | 0 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:03 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:08 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:14 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:19 | 0 | 0 | 0 | 434 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:24 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:29 | 0 | 0 | 0 | 434 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:34 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:39 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:45 | 0 | 0 | 0 | 434 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:50 | 0 | 0 | 0 | 435 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:30:55 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:00 | 0 | 0 | 0 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:05 | 0 | 0 | 0 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:10 | 0 | 0 | 0 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:16 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:21 | 0 | 0 | 0 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:26 | 0 | 0 | 0 | 436 | 435 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:31:58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:48 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:53 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:32:58 | 3.2 | 3.2 | 3.2 | 438 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:03 | 7.7 | 7.7 | 7.7 | 438 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:09 | 7.8 | 7.7 | 7.7 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:14 | 7.7 | 7.7 | 7.7 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:19 | 7.7 | 7.7 | 7.7 | 440 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:24 | 7.7 | 7.7 | 7.7 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:30 | 7.7 | 7.7 | 7.7 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:36 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:41 | 7.7 | 7.7 | 7.7 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:46 | 7.7 | 7.7 | 7.7 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:52 | 7.7 | 7.7 | 7.7 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:33:58 | 7.7 | 7.7 | 7.7 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:03 | 7.7 | 7.7 | 7.7 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:11 | 7.8 | 7.7 | 7.8 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:16 | 7.8 | 7.7 | 7.8 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:21 | 7.8 | 7.7 | 7.8 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:26 | 7.8 | 7.7 | 7.8 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:31 | 7.8 | 7.8 | 7.8 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:36 | 7.8 | 7.7 | 7.8 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:42 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:47 | 7.8 | 7.7 | 7.8 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:52 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:34:57 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:02 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:07 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:13 | 7.7 | 7.7 | 7.7 | 441 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:18 | 7.8 | 7.7 | 7.7 | 441 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:23 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:28 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:34 | 7.8 | 7.7 | 7.8 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:41 | 7.8 | 7.7 | 7.8 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:46 | 7.8 | 7.7 | 7.8 | 442 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:51 | 7.8 | 7.7 | 7.7 | 442 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:35:57 | 7.8 | 7.7 | 7.7 | 442 | 442 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:02 | 7.8 | 7.7 | 7.7 | 442 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:08 | 7.7 | 7.7 | 7.7 | 442 | 441 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:13 | 7.7 | 7.7 | 7.7 | 441 | 441 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:18 | 7.7 | 7.7 | 7.7 | 441 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:23 | 7.7 | 7.7 | 7.7 | 441 | 441 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:29 | 7.7 | 7.7 | 7.7 | 441 | 441 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:34 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:40 | 7.8 | 7.7 | 7.7 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:45 | 7.8 | 7.7 | 7.7 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:50 | 7.8 | 7.7 | 7.7 | 441 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:36:55 | 7.7 | 7.7 | 7.7 | 441 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:01 | 7.7 | 7.7 | 7.7 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:08 | 7.8 | 7.7 | 7.7 | 441 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:13 | 7.8 | 7.7 | 7.7 | 441 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:18 | 7.8 | 7.7 | 7.7 | 441 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:24 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:30 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:35 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:41 | 7.7 | 7.7 | 7.7 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:46 | 7.7 | 7.7 | 7.7 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:53 | 7.7 | 7.7 | 7.7 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:37:58 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:23 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:28 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:33 | 0 | 0 | 0 | 437 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:38 | 0 | 0 | 0 | 438 | 438 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:38:53 | 0 | 0 | 0 | 438 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:02 | 0 | 0 | 0 | 438 | 438 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:08 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:13 | 0 | 0 | 0 | 438 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:18 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:23 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:28 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:38 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:48 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:54 | 0 | 0 | 0 | 440 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:40:59 | 0 | 0 | 0 | 439 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:05 | 0 | 0 | 0 | 440 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:10 | 0 | 0 | 0 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:15 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:20 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:25 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:31 | 0 | 0 | 0 | 439 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:36 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:42 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:47 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:52 | 0 | 0 | 0 | 439 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:41:59 | 0 | 0 | 0 | 438 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:05 | 0 | 0 | 0 | 438 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:11 | 0 | 0 | 0 | 438 | 437 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:16 | 0 | 0 | 0 | 438 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:22 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:27 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:32 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:37 | 0 | 0 | 0 | 440 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:42 | 0 | 0 | 0 | 440 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:47 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:54 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:42:59 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:04 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:07 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:17 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:33 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:38 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:43 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:48 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:53 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:43:59 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:04 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:09 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:14 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:19 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:25 | 0 | 0 | 0 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:30 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:35 | 0 | 0 | 0 | 440 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:40 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:45 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:50 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:44:56 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:01 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:06 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:11 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:16 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:22 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:27 | 0 | 0 | 0 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:32 | 0 | 0 | 0 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:37 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:42 | 0 | 0 | 0 | 442 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:48 | 0 | 0 | 0 | 442 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:53 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:45:58 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:03 | 0 | 0 | 0 | 441 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:08 | 0 | 0 | 0 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:13 | 0 | 0 | 0 | 441 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:19 | 0 | 0 | 0 | 442 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:24 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:29 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:36 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:42 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:47 | 0 | 0 | 0 | 442 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:52 | 0 | 0 | 0 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:46:57 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:47:02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:47:37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:47:42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:47:52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:47:57 | 0 | 0 | 0 | 434 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:03 | 0 | 0 | 0 | 435 | 434 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:13 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:23 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:28 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:33 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:38 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:44 | 0 | 0 | 0 | 434 | 434 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:49 | 0 | 0 | 0 | 434 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:48:55 | 0 | 0 | 0 | 434 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:00 | 0 | 0 | 0 | 433 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:05 | 0 | 0 | 0 | 433 | 432 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:10 | 0 | 0 | 0 | 433 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:15 | 0 | 0 | 0 | 434 | 433 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:20 | 0 | 0 | 0 | 430 | 430 | 431 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:40 | 0 | 0 | 0 | 430 | 430 | 431 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:45 | 0 | 0 | 0 | 430 | 430 | 431 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:49:54 | 0 | 0 | 0 | 431 | 431 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:04 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:09 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:14 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:20 | 0 | 0 | 0 | 434 | 434 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:25 | 0 | 0 | 0 | 434 | 434 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:30 | 0 | 0 | 0 | 434 | 434 | 434 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:35 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:40 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:50:45 | 0 | 0 | 0 | 434 | 434 | 435 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:27 | 0 | 0 | 0 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:32 | 0 | 0 | 0 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:37 | 0 | 0 | 0 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:44 | 0 | 0 | 0 | 436 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:49 | 0 | 0 | 0 | 436 | 434 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:55:54 | [11 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T15:57:06 | 0 | 0 | 0 | 435 | 434 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:16 | 0 | 0 | 0 | 436 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:22 | 0 | 0 | 0 | 436 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:27 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:32 | 0 | 0 | 0 | 436 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:37 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:42 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:47 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:52 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:57:58 | 0 | 0 | 0 | 438 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:03 | 0 | 0 | 0 | 438 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:08 | 0 | 0 | 0 | 438 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:13 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:18 | 0 | 0 | 0 | 437 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:23 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:29 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:34 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:39 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:44 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:49 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:58:54 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:00 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:06 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:11 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:16 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:21 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:26 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:32 | 0 | 0 | 0 | 335 | 335 | 336 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T15:59:59 | 0 | 0 | 0 | 441 | 441 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:05 | 0 | 0 | 0 | 445 | 445 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:10 | 0 | 0 | 0 | 445 | 445 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:15 | 0 | 0 | 0 | 445 | 445 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:20 | 0 | 0 | 0 | 445 | 445 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:25 | 0 | 0 | 0 | 445 | 445 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:31 | 0 | 0 | 0 | 446 | 446 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:37 | 0 | 0 | 0 | 446 | 446 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:42 | 0 | 0 | 0 | 445 | 446 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:47 | 0 | 0 | 0 | 445 | 446 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:52 | 0 | 0 | 0 | 446 | 447 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:00:57 | 0 | 0 | 0 | 446 | 447 | 447 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:03 | 0 | 0 | 0 | 221 | 445 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:08 | 0 | 0 | 0 | 221 | 445 | 225 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:13 | 0 | 0 | 0 | 221 | 445 | 225 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:18 | 0 | 0 | 0 | 221 | 445 | 225 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:23 | 0 | 0 | 0 | 222 | 446 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:28 | 0 | 0 | 0 | 222 | 446 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:34 | 0 | 0 | 0 | 222 | 446 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:39 | 0 | 0 | 0 | 221 | 445 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:44 | 0 | 0 | 0 | 222 | 446 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:49 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:54 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:01:59 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:05 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:10 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:15 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:20 | 0 | 0 | 0 | 222 | 448 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:25 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:30 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:35 | 0 | 0 | 0 | 222 | 448 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:41 | 0 | 0 | 0 | 222 | 448 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:46 | 0 | 0 | 0 | 222 | 448 | 227 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:51 | 0 | 0 | 0 | 222 | 448 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:02:56 | 0 | 0 | 0 | 222 | 448 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:01 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:06 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:12 | 0 | 0 | 0 | 222 | 447 | 226 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:17 | 0 | 0 | 0 | 449 | 449 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:22 | 0 | 0 | 0 | 449 | 449 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:27 | 39.1 | 39 | 39.1 | 449 | 448 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:32 | 39.4 | 39.2 | 39.4 | 448 | 448 | 450 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:38 | 38.5 | 38.4 | 38.5 | 447 | 447 | 450 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:43 | 38.2 | 38.1 | 38.2 | 449 | 448 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:49 | 38.2 | 38 | 38.1 | 448 | 447 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:54 | 37.8 | 37.7 | 37.8 | 449 | 448 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:03:59 | 37.8 | 37.7 | 37.8 | 448 | 448 | 450 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:04 | 37.6 | 37.5 | 37.6 | 449 | 449 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:09 | 37.7 | 37.6 | 37.7 | 449 | 449 | 451 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:15 |  |  | 0 | 0 | 0 | [6 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T16:04:29 | 18 | 17.9 | 18 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:35 | 18 | 17.9 | 18 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:40 | 18 | 17.9 | 18 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:04:45 | 18 | 18 | 18 | 437 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 1
2026-08-27T16:04:50 | 18 | 18 | 18 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 1
2026-08-27T16:04:55 | 13.5 | 13.5 | 13.5 | 436 | 436 | 438 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 1
2026-08-27T16:05:01 | 12.2 | 12.2 | 12.2 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 1
2026-08-27T16:05:06 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 1
2026-08-27T16:05:11 | 12.2 | 12.2 | 12.2 | 435 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:17 | 12.2 | 12.2 | 12.2 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:23 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:28 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:33 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:38 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:43 | 12.2 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:49 | 12.3 | 12.2 | 12.2 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:54 | 12.3 | 12.2 | 12.3 | 436 | 436 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:05:59 | 12.3 | 12.2 | 12.2 | 436 | 436 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:04 | 12.3 | 12.2 | 12.2 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:09 | 12.3 | 12.2 | 12.3 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:15 | 12.3 | 12.2 | 12.2 | 436 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:20 | 12.3 | 12.2 | 12.2 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:25 | 12.3 | 12.2 | 12.3 | 436 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 1
2026-08-27T16:06:30 | 12.3 | 12.2 | 12.3 | 436 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T16:06:35 | 12.3 | 12.2 | 12.3 | 435 | 435 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T16:06:41 | 12.3 | 12.2 | 12.3 | 435 | 434 | 436 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T16:06:47 | 12.3 | 12.2 | 12.3 | 435 | 435 | 437 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:04 | 0 | 0 | 0 | 530 | 530 | 533 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:09 | 0 | 0 | 0 | 530 | 530 | 533 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:14 | 0 | 0 | 0 | 530 | 531 | 533 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:19 | 0 | 0 | 0 | 530 | 531 | 532 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:24 | 0 | 0 | 0 | 531 | 533 | 534 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:31 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:36 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:43 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 0
2026-08-27T17:08:49 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 1 | 0
2026-08-27T17:08:54 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:08:59 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:04 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:10 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:15 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:20 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:25 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:32 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:38 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:43 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:48 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:53 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:09:59 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 18 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:04 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:09 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:14 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:21 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:26 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:31 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:36 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:43 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:48 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:53 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:10:58 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18.1 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:03 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 18.1 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:09 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 19.1 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:15 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 19.1 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:21 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 19.1 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:26 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:32 | 0 | 0 | 0 | 439 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:37 | 0 | 0 | 0 | 439 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:42 | 0 | 0 | 0 | 439 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:48 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:53 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:11:58 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:04 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:10 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:15 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:20 | 0 | 0 | 0 | 438 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:25 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:30 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:36 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:41 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:46 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:51 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:12:56 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:02 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:07 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 44 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:12 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 44 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:17 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 44 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:23 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 44 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:30 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 44 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:35 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 158 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:40 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 158 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:45 | 0 | 0 | 0 | 439 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 158 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:51 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 158 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:13:56 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:01 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:06 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:11 | 0 | 0 | 0 | 432 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:17 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:22 | 0 | 0 | 0 | 431 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:27 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 10 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:32 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 30 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:37 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 30 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:43 | 0 | 0 | 0 | 432 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 30 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:48 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 40 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:14:55 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 41 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:00 | 0 | 0 | 0 | 430 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 41 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:07 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 41 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:12 | 0 | 0 | 0 | 430 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 41 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:18 | 0 | 0 | 0 | 431 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 41 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:23 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:28 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:33 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:38 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:44 | 0 | 0 | 0 | 431 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:50 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:15:56 | 0 | 0 | 0 | 431 | 432 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:01 | 0 | 0 | 0 | 431 | 431 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:06 | 0 | 0 | 0 | 431 | 432 | 433 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:12 | 0 | 0 | 0 | 431 | 431 | 432 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:17 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:22 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:27 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:34 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:39 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:45 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:50 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:16:55 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:00 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:05 | 0 | 0 | 0 | 440 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:11 | 0 | 0 | 0 | 439 | 440 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:17 | 0 | 0 | 0 | 440 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:22 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:27 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:33 | 0 | 0 | 0 | 438 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:38 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:43 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:48 | 0 | 0 | 0 | 438 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:17:53 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:00 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:05 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:10 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:15 | 0 | 0 | 0 | 438 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:20 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:26 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:31 | 0 | 0 | 0 | 438 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:36 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:42 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:48 | 0 | 0 | 0 | 437 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:53 | 0 | 0 | 0 | 437 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:18:59 | 0 | 0 | 0 | 437 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:04 | 0 | 0 | 0 | 436 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:09 | 0 | 0 | 0 | 436 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:15 | 0 | 0 | 0 | 436 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:20 | 0 | 0 | 0 | 436 | 437 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:25 | 0 | 0 | 0 | 437 | 438 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:30 | 0 | 0 | 0 | 437 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:35 | 0 | 0 | 0 | 437 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:41 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:46 | 0 | 0 | 0 | 437 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:51 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:19:56 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:20:01 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:20:08 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:20:12 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:20:17 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 51 | 0 | 0
2026-08-27T17:20:22 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:27 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:33 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:39 | 0 | 0 | 0 | 439 | 440 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:44 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:50 | 0 | 0 | 0 | 439 | 439 | 439 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:20:57 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:21:02 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:21:07 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:21:13 | 0 | 0 | 0 | 439 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:21:20 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0
2026-08-27T17:21:25 |  |  | 0 | 438 | 0 | [6 empty] | 1 |  |  |  |  | 1 |  | 0
2026-08-27T17:21:42 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T17:21:47 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 1 | 1
2026-08-27T17:21:52 | 0 | 0 | 0 | 439 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:21:58 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:03 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:08 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:14 | 0 | 0 | 0 | 438 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:19 | 0 | 0 | 0 | 438 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:24 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:29 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:34 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:39 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:45 | 0 | 0 | 0 | 438 | 439 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:51 | 0 | 0 | 0 | 438 | 438 | 440 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:22:57 | 0 | 0 | 0 | 438 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:23:02 | 0 | 0 | 0 | 437 | 439 | 441 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:10 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:15 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:22 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:28 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:33 | 0 | 0 | 0 | 439 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:38 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:43 | 0 | 0 | 0 | 440 | 440 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:49 | 0 | 0 | 0 | 440 | 440 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:54 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:34:59 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:04 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:09 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:14 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:21 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:29 | 0 | 0 | 0 | 441 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:35 | 0 | 0 | 0 | 441 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:40 | 0 | 0 | 0 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:45 | 0 | 0 | 0 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:50 | 0 | 0 | 0 | 442 | 442 | 444 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:35:56 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:01 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:06 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:11 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:16 | 0 | 0 | 0 | 441 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:21 | 0 | 0 | 0 | 441 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:27 | 0 | 0 | 0 | 442 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:33 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:38 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:43 | 0 | 0 | 0 | 440 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:48 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:54 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:36:59 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:37:05 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:37:11 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:37:16 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:37:21 | 0 | 0 | 0 | 440 | 440 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 1
2026-08-27T17:37:27 | 0 | 0 | 0 | 441 | 441 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 1 | 0
2026-08-27T17:37:32 | 0 | 0 | 0 | 441 | 441 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 1 | 0
2026-08-27T17:37:38 | 0 | 0 | 0 | 442 | 442 | 443 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 1 | 0
2026-08-27T17:37:43 | 0 | 0 | 0 | 442 | 442 | 442 | 0 | 12 | 0 | 101 | 15 | 1 | 20 | 20.5 | 57 | 1 | 1 | 0 | 0 | 102 | 0 | 0

## Phase Analysis
Timestamp | Voltage Imbalance % | Current Imbalance %
2026-08-25T14:24:47 |  | 22.95
2026-08-25T14:24:52 |  | 22.22
2026-08-25T14:24:58 |  | 23.32
2026-08-25T14:25:04 |  | 23.68
2026-08-25T14:25:10 |  | 23.68
2026-08-25T14:25:15 |  | 21.14
2026-08-25T14:25:20 |  | 88.14
2026-08-25T14:25:26 |  | 134.15
2026-08-25T14:25:31 |  | 134.15
2026-08-25T14:25:36 |  | 134.15
2026-08-25T14:25:42 |  | 134.15
2026-08-25T14:25:47 |  | 134.15
2026-08-25T14:25:53 |  | 134.15
2026-08-25T14:25:59 |  | 133.33
2026-08-25T14:26:04 |  | 134.15
2026-08-25T14:26:10 |  | 134.15
2026-08-25T14:26:15 |  | 134.15
2026-08-25T14:26:21 |  | 134.15
2026-08-25T14:26:26 |  | 134.15
2026-08-25T14:26:31 |  | 133.33
2026-08-25T14:26:37 |  | 133.33
2026-08-25T14:26:42 |  | 133.33
2026-08-25T14:26:47 |  | 133.33
2026-08-25T14:26:54 |  | 133.33
2026-08-25T14:26:59 |  | 133.33
2026-08-25T14:27:05 |  | 133.33
2026-08-25T14:27:10 |  | 133.33
2026-08-25T14:27:15 |  | 133.33
2026-08-25T14:27:21 |  | 133.33
2026-08-25T14:27:26 |  | 133.33
2026-08-25T14:27:32 |  | 133.33
2026-08-25T14:27:37 |  | 133.33
2026-08-25T14:27:42 |  | 132.52
2026-08-25T14:27:49
2026-08-25T14:27:54
2026-08-25T14:27:59
2026-08-25T14:28:04
2026-08-25T14:28:09
2026-08-25T14:28:14
2026-08-25T14:28:19
2026-08-25T14:28:24
2026-08-25T14:28:29
2026-08-25T14:28:34
2026-08-25T14:28:39
2026-08-25T14:28:44
2026-08-25T14:28:49
2026-08-25T14:28:54
2026-08-25T14:28:59
2026-08-25T14:29:04
2026-08-25T14:29:09
2026-08-25T14:29:14
2026-08-25T14:29:19
2026-08-25T14:29:24
2026-08-25T14:29:29
2026-08-25T14:29:34
2026-08-25T14:29:39
2026-08-25T14:29:44
2026-08-25T14:29:49
2026-08-25T14:29:54
2026-08-25T14:29:59
2026-08-25T14:30:04
2026-08-25T14:30:09
2026-08-25T14:30:14
2026-08-25T14:30:19
2026-08-25T14:30:24
2026-08-25T14:30:29
2026-08-25T14:30:34
2026-08-25T14:30:39
2026-08-25T14:30:44
2026-08-25T14:30:49
2026-08-25T14:30:54
2026-08-25T14:30:59
2026-08-25T14:31:04
2026-08-25T14:31:10
2026-08-25T14:32:29
2026-08-25T14:32:35
2026-08-25T14:32:40
2026-08-25T14:32:45
2026-08-25T14:32:50
2026-08-25T14:32:55
2026-08-25T14:33:00
2026-08-25T14:33:05
2026-08-25T14:33:10
2026-08-25T14:33:15
2026-08-25T14:33:20
2026-08-25T14:33:25
2026-08-25T14:33:30
2026-08-25T14:33:35
2026-08-25T14:33:40
2026-08-25T14:33:45
2026-08-25T14:33:50
2026-08-25T14:33:55
2026-08-25T14:34:00
2026-08-25T14:34:05
2026-08-25T14:34:10
2026-08-25T14:34:15
2026-08-25T14:34:20
2026-08-25T14:34:25
2026-08-25T14:34:30
2026-08-25T14:34:35
2026-08-25T14:34:40
2026-08-25T14:34:45
2026-08-25T14:34:50
2026-08-25T14:34:55
2026-08-25T14:35:00
2026-08-25T14:35:05
2026-08-25T15:13:30 |  | 200
2026-08-25T15:13:35 |  | 200
2026-08-25T15:13:41 |  | 200
2026-08-25T15:13:46 |  | 200
2026-08-25T15:13:52 |  | 200
2026-08-25T15:13:59 |  | 200
2026-08-25T15:14:04 |  | 200
2026-08-25T15:14:11 |  | 200
2026-08-25T15:15:00 |  | 200
2026-08-25T15:15:05 |  | 200
2026-08-25T15:15:12 |  | 200
2026-08-25T15:15:18 |  | 200
2026-08-25T15:15:24 |  | 200
2026-08-25T15:15:30 |  | 200
2026-08-25T15:15:35 |  | 200
2026-08-25T15:15:41 |  | 200
2026-08-25T15:15:47 |  | 200
2026-08-25T15:15:53 |  | 200
2026-08-25T15:15:59 |  | 200
2026-08-25T15:16:06 |  | 200
2026-08-25T15:16:11 |  | 300
2026-08-25T15:16:18 |  | 200
2026-08-25T15:16:23 |  | 200
2026-08-25T15:16:29 |  | 200
2026-08-25T15:16:35 |  | 200
2026-08-25T15:16:40 |  | 200
2026-08-25T15:16:46 |  | 200
2026-08-25T15:16:52 |  | 200
2026-08-25T15:16:57 |  | 200
2026-08-25T15:17:03 |  | 200
2026-08-25T15:17:08 |  | 200
2026-08-25T15:17:14 |  | 200
2026-08-25T15:17:20 |  | 200
2026-08-25T15:17:26 |  | 200
2026-08-25T15:17:32 |  | 200
2026-08-25T15:17:39 |  | 200
2026-08-25T15:17:44 |  | 200
2026-08-25T15:17:51 |  | 200
2026-08-25T15:17:56 |  | 200
2026-08-25T15:18:03 |  | 200
2026-08-25T15:18:09 |  | 200
2026-08-25T15:18:15 |  | 200
2026-08-25T15:18:21
2026-08-25T15:18:26
2026-08-25T15:18:32
2026-08-25T15:18:37
2026-08-25T15:18:42
2026-08-25T15:18:48
2026-08-25T15:18:53
2026-08-25T15:18:58
2026-08-25T15:19:04
2026-08-25T15:19:09
2026-08-25T15:19:14
2026-08-25T15:19:20
2026-08-25T15:19:25
2026-08-25T15:19:30
2026-08-25T15:19:36
2026-08-25T15:19:41
2026-08-25T15:19:46
2026-08-25T15:19:52
2026-08-25T15:19:57
2026-08-25T15:20:02
2026-08-25T15:20:08
2026-08-25T15:20:13
2026-08-25T15:20:18
2026-08-25T15:20:24
2026-08-25T15:20:29
2026-08-25T15:20:34
2026-08-25T15:20:40
2026-08-25T15:20:58 |  | 200
2026-08-25T15:21:04 |  | 200
2026-08-25T15:21:15 |  | 200
2026-08-25T15:21:21 |  | 200
2026-08-25T15:21:26 |  | 200
2026-08-25T15:21:32 |  | 200
2026-08-25T15:21:38 |  | 200
2026-08-25T15:21:43 |  | 200
2026-08-25T15:21:49 |  | 200
2026-08-25T15:21:54 |  | 200
2026-08-25T15:22:00 |  | 200
2026-08-25T15:22:07 |  | 200
2026-08-25T15:22:12 |  | 200
2026-08-25T15:22:19 |  | 200
2026-08-25T15:22:25 |  | 200
2026-08-25T15:22:30 |  | 200
2026-08-25T15:22:36 |  | 200
2026-08-25T15:22:47 |  | 200
2026-08-25T15:22:52 |  | 200
2026-08-25T15:22:58 |  | 200
2026-08-25T15:23:04 |  | 200
2026-08-25T15:23:09 |  | 200
2026-08-25T15:23:15 |  | 200
2026-08-25T15:23:20 |  | 200
2026-08-25T15:23:26 |  | 200
2026-08-25T15:23:32 |  | 200
2026-08-25T15:23:37 |  | 200
2026-08-25T15:23:43 |  | 200
2026-08-25T15:23:49 |  | 200
2026-08-25T15:23:55 |  | 200
2026-08-25T15:24:01 |  | 200
2026-08-25T15:24:07 |  | 200
2026-08-25T15:24:13 |  | 200
2026-08-25T15:24:19 |  | 200
2026-08-25T15:24:25 |  | 200
2026-08-25T15:24:37 |  | 200
2026-08-25T15:24:42 |  | 128.5
2026-08-25T15:24:48 |  | 127.71
2026-08-25T15:24:53 |  | 127.71
2026-08-25T15:24:59 |  | 127.71
2026-08-25T15:25:05 |  | 128.5
2026-08-25T15:25:10 |  | 128.5
2026-08-25T15:25:16 |  | 128.5
2026-08-25T15:25:22 | 200 | 128.5
2026-08-25T15:25:27 |  | 127.71
2026-08-25T15:25:33 |  | 128.5
2026-08-25T15:25:38 |  | 128.5
2026-08-25T15:25:45 |  | 127.71
2026-08-25T15:25:51 |  | 128.5
2026-08-25T15:26:02 |  | 127.71
2026-08-25T15:26:08 |  | 128.5
2026-08-25T15:26:13 |  | 128.5
2026-08-25T15:26:19 |  | 128.5
2026-08-25T15:26:24 |  | 128.5
2026-08-25T15:26:30 |  | 128.5
2026-08-25T15:26:36 |  | 128.5
2026-08-25T15:26:41 |  | 128.5
2026-08-25T15:26:47 |  | 128.5
2026-08-25T15:26:53 |  | 128.5
2026-08-25T15:26:58 |  | 128.5
2026-08-25T15:27:09 |  | 128.5
2026-08-25T15:27:15 |  | 128.5
2026-08-25T15:27:20 |  | 128.5
2026-08-25T15:27:26 |  | 128.5
2026-08-25T15:27:32 |  | 128.5
2026-08-25T15:33:53 |  | 128.5
2026-08-25T15:33:58 |  | 128.5
2026-08-25T15:34:05 |  | 128.5
2026-08-25T15:34:16 |  | 128.5
2026-08-25T15:34:22 |  | 128.5
2026-08-25T15:45:44
2026-08-25T15:45:50
2026-08-25T15:45:56
2026-08-25T15:46:02
2026-08-25T15:46:08
2026-08-25T15:46:14
2026-08-25T15:46:20
2026-08-25T15:46:25
2026-08-25T15:48:44
2026-08-25T15:48:51
2026-08-25T15:48:58
2026-08-25T15:49:04
2026-08-25T15:49:10
2026-08-25T15:49:16
2026-08-25T15:49:21
2026-08-25T15:49:28
2026-08-25T15:49:34
2026-08-25T15:49:40
2026-08-25T15:49:46
2026-08-25T15:49:52
2026-08-25T15:49:59
2026-08-25T15:50:05
2026-08-25T15:50:10
2026-08-25T15:50:16
2026-08-25T15:50:23
2026-08-25T15:50:29
2026-08-25T15:50:35
2026-08-25T15:50:41
2026-08-25T15:50:47
2026-08-25T15:50:53
2026-08-25T15:50:59
2026-08-25T15:51:05
2026-08-25T15:51:12
2026-08-25T15:51:18
2026-08-25T15:51:24
2026-08-25T15:51:30
2026-08-25T15:51:36
2026-08-25T15:51:42
2026-08-25T15:51:49
2026-08-25T15:51:54
2026-08-25T15:55:29 |  | 217.24
2026-08-25T15:55:34 |  | 217.24
2026-08-25T15:55:40 |  | 217.24
2026-08-25T15:55:45 |  | 217.24
2026-08-25T15:55:50 |  | 217.24
2026-08-25T15:55:55 |  | 217.24
2026-08-25T15:56:00 |  | 217.24
2026-08-25T15:56:05 |  | 217.24
2026-08-25T15:56:10 |  | 217.24
2026-08-25T15:56:15 |  | 217.24
2026-08-25T15:56:20 |  | 217.24
2026-08-25T15:56:25 |  | 217.24
2026-08-25T15:56:31 |  | 217.24
2026-08-25T15:56:36 |  | 217.24
2026-08-25T15:56:41 |  | 217.24
2026-08-25T15:56:46 |  | 217.24
2026-08-25T15:56:51 |  | 217.24
2026-08-25T15:56:56 |  | 217.24
2026-08-25T15:57:01 |  | 217.24
2026-08-25T15:57:06 |  | 217.24
2026-08-25T15:57:11 |  | 217.24
2026-08-25T15:57:16 |  | 217.24
2026-08-25T15:57:22 |  | 217.24
2026-08-25T15:57:27 |  | 217.24
2026-08-25T15:57:32 |  | 217.24
2026-08-25T15:57:37 |  | 217.24
2026-08-25T15:57:42 |  | 217.24
2026-08-25T15:57:47
2026-08-25T15:57:52
2026-08-25T15:57:58
2026-08-25T15:58:03
2026-08-25T15:58:08
2026-08-25T15:58:14
2026-08-25T15:58:19
2026-08-25T15:58:24
2026-08-25T15:58:30
2026-08-25T15:58:35
2026-08-25T15:58:40
2026-08-25T15:58:46
2026-08-25T15:58:51
2026-08-25T15:58:56
2026-08-25T15:59:03 |  | 217.24
2026-08-25T15:59:08 |  | 217.24
2026-08-25T15:59:13 |  | 217.24
2026-08-25T15:59:18 |  | 217.24
2026-08-25T15:59:24 |  | 217.24
2026-08-25T15:59:29 |  | 217.24
2026-08-25T15:59:34 |  | 217.24
2026-08-25T15:59:39 |  | 217.24
2026-08-25T15:59:44 |  | 217.24
2026-08-25T15:59:49 |  | 217.24
2026-08-25T15:59:54 |  | 217.24
2026-08-25T15:59:59 |  | 217.24
2026-08-25T16:00:04 |  | 217.24
2026-08-25T16:00:10 |  | 217.24
2026-08-25T16:00:15 |  | 217.24
2026-08-25T16:00:20 |  | 217.24
2026-08-25T16:00:25 |  | 217.24
2026-08-25T16:00:30 |  | 217.24
2026-08-25T16:00:35 |  | 217.24
2026-08-25T16:00:40 |  | 217.24
2026-08-25T16:00:45 |  | 217.24
2026-08-25T16:00:50 |  | 217.24
2026-08-25T16:00:55 |  | 217.24
2026-08-25T16:01:01 |  | 217.24
2026-08-25T16:01:06 |  | 217.24
2026-08-25T16:01:11 |  | 217.24
2026-08-25T16:01:16 |  | 217.24
2026-08-25T16:01:21 |  | 217.24
2026-08-25T16:01:26 |  | 217.24
2026-08-25T16:01:31 |  | 217.24
2026-08-25T16:01:36 |  | 217.24
2026-08-25T16:01:41 |  | 217.24
2026-08-25T16:01:46 |  | 217.24
2026-08-25T16:01:52 |  | 217.24
2026-08-25T16:01:57 |  | 217.24
2026-08-25T16:02:02 |  | 217.24
2026-08-25T16:02:07 |  | 217.24
2026-08-25T16:02:12 |  | 217.24
2026-08-25T16:02:17 |  | 217.24
2026-08-25T16:02:22 |  | 217.24
2026-08-25T16:02:27 |  | 217.24
2026-08-25T16:02:32 |  | 217.24
2026-08-25T16:02:38 |  | 217.24
2026-08-25T16:02:43 |  | 217.24
2026-08-25T16:02:48 |  | 217.24
2026-08-25T16:02:53 |  | 217.24
2026-08-25T16:02:58 |  | 217.24
2026-08-25T16:03:03 |  | 217.24
2026-08-25T16:03:08 |  | 217.24
2026-08-25T16:03:13 |  | 217.24
2026-08-25T16:03:18 |  | 217.24
2026-08-25T16:03:23 |  | 217.24
2026-08-25T16:03:29 |  | 217.24
2026-08-25T16:03:34 |  | 217.24
2026-08-25T16:03:39 |  | 217.24
2026-08-25T16:03:44 |  | 217.24
2026-08-25T16:07:28 |  | 217.24
2026-08-25T16:07:33 |  | 217.24
2026-08-25T16:07:38 |  | 217.24
2026-08-25T16:07:43 |  | 217.24
2026-08-25T16:07:48 |  | 217.24
2026-08-25T16:07:54 |  | 217.24
2026-08-25T16:07:59 |  | 217.24
2026-08-25T16:08:04 |  | 217.24
2026-08-25T16:08:09 |  | 173.3
2026-08-25T16:08:15 |  | 217.24
2026-08-25T16:08:20 |  | 217.24
2026-08-25T16:08:25
2026-08-25T16:08:31
2026-08-25T16:08:36
2026-08-25T16:08:41
2026-08-25T16:08:47
2026-08-25T16:08:52
2026-08-25T16:08:57
2026-08-25T16:09:03
2026-08-25T16:09:08
2026-08-25T16:09:14 |  | 217.24
2026-08-25T16:09:19 |  | 217.24
2026-08-25T16:09:24 |  | 217.24
2026-08-25T16:09:29 |  | 217.24
2026-08-25T16:09:34 |  | 217.24
2026-08-25T16:09:40 |  | 217.24
2026-08-25T16:09:46 |  | 217.24
2026-08-25T16:09:53 |  | 217.24
2026-08-25T16:09:59 |  | 217.24
2026-08-25T16:10:05 |  | 217.24
2026-08-25T16:10:10 |  | 217.24
2026-08-25T16:10:15 |  | 217.24
2026-08-25T16:10:20 |  | 217.24
2026-08-25T16:10:25 |  | 217.24
2026-08-25T16:10:30 |  | 217.24
2026-08-25T16:10:35 |  | 217.24
2026-08-25T16:10:40 |  | 217.24
2026-08-25T16:10:46 |  | 217.24
2026-08-25T16:10:51 |  | 217.24
2026-08-25T16:10:56 |  | 217.24
2026-08-25T16:11:01 |  | 217.24
2026-08-25T16:11:06 |  | 217.24
2026-08-25T16:11:11 |  | 217.24
2026-08-25T16:11:16 |  | 217.24
2026-08-25T16:11:21 |  | 217.24
2026-08-25T16:11:26 |  | 217.24
2026-08-25T16:11:31 |  | 217.24
2026-08-25T16:11:36 |  | 217.24
2026-08-25T16:11:42 |  | 217.24
2026-08-25T16:11:47 |  | 217.24
2026-08-25T16:11:52 |  | 217.24
2026-08-25T16:11:57 |  | 217.24
2026-08-25T16:12:02 |  | 217.24
2026-08-25T16:12:07 |  | 217.24
2026-08-25T16:12:12 |  | 217.24
2026-08-25T16:12:17 |  | 217.24
2026-08-25T16:12:22 |  | 217.24
2026-08-25T16:12:27 |  | 217.24
2026-08-25T16:12:33 |  | 217.24
2026-08-25T16:12:38 |  | 217.24
2026-08-25T16:12:43 |  | 217.24
2026-08-25T16:12:48 |  | 217.24
2026-08-25T16:12:53 |  | 217.24
2026-08-25T16:12:58 |  | 217.24
2026-08-25T16:13:03 |  | 217.24
2026-08-25T16:13:08 |  | 217.24
2026-08-25T16:13:13 |  | 217.24
2026-08-25T16:13:18 |  | 217.24
2026-08-25T16:13:23 |  | 217.24
2026-08-25T16:13:29 |  | 217.24
2026-08-25T16:13:34 |  | 217.24
2026-08-25T16:13:40 |  | 217.24
2026-08-25T16:13:45 |  | 217.24
2026-08-25T16:13:50 |  | 217.24
2026-08-25T16:13:55 |  | 217.24
2026-08-25T16:14:00 |  | 217.24
2026-08-25T16:14:05 |  | 217.24
2026-08-25T16:14:10 |  | 217.24
2026-08-25T16:14:15 |  | 217.24
2026-08-25T16:14:21 |  | 217.24
2026-08-25T16:14:26 |  | 217.24
2026-08-25T16:14:31 |  | 217.24
2026-08-25T16:14:36
2026-08-25T16:14:41
2026-08-25T16:14:47
2026-08-25T16:14:52
2026-08-25T16:14:57
2026-08-25T16:15:03
2026-08-25T16:15:08
2026-08-25T16:15:13
2026-08-25T16:15:19
2026-08-25T16:15:24
2026-08-25T16:15:29
2026-08-25T16:15:35
2026-08-25T16:15:40
2026-08-25T16:15:45
2026-08-25T16:15:51
2026-08-25T16:15:56
2026-08-25T16:16:01
2026-08-25T16:16:07
2026-08-25T16:16:12
2026-08-25T16:16:17 | 126.8 | 208.47
2026-08-25T16:16:22 | 126.66 | 221.74
2026-08-25T16:16:27 | 126.85 | 208.47
2026-08-25T16:16:33 | 126.85 | 208.47
2026-08-25T16:16:38 | 126.44 | 221.74
2026-08-25T16:16:43 | 126.71 | 208.47
2026-08-25T16:16:49 | 126.71 | 208.47
2026-08-25T16:16:54 | 126.85 | 221.74
2026-08-25T16:16:59 | 126.66 | 221.74
2026-08-25T16:17:04 | 126.71 | 221.74
2026-08-25T16:17:09 | 126.71 | 221.74
2026-08-25T16:17:14 | 126.71 | 208.47
2026-08-25T16:17:19 | 126.52 | 208.47
2026-08-25T16:17:25 | 126.52 | 208.47
2026-08-25T16:17:30 | 126.52 | 221.74
2026-08-25T16:17:35 | 126.71 | 221.74
2026-08-25T16:17:40 | 115.36 | 208.47
2026-08-25T16:17:45 | 110.38 | 221.74
2026-08-25T16:17:50 | 110.38 | 221.74
2026-08-25T16:17:55 | 110.46 | 208.47
2026-08-25T16:18:00 | 110.66 | 221.74
2026-08-25T16:18:05 | 110.66 | 221.74
2026-08-25T16:18:10 | 110.77 | 221.74
2026-08-25T16:18:15 | 110.46 | 208.47
2026-08-25T16:18:21 | 110.89 | 208.47
2026-08-25T16:18:26 | 110.89 | 221.74
2026-08-25T16:18:31 | 110.89 | 208.47
2026-08-25T16:18:36 | 111.01 | 221.74
2026-08-25T16:19:19
2026-08-25T16:20:17 |  | 298.2
2026-08-25T16:20:50
2026-08-25T16:20:55
2026-08-25T16:21:01
2026-08-25T16:21:06
2026-08-25T16:21:11
2026-08-25T16:21:17
2026-08-25T16:21:22
2026-08-25T16:21:27
2026-08-25T16:21:33
2026-08-25T16:21:38
2026-08-25T16:21:43
2026-08-25T16:21:48
2026-08-25T16:21:54
2026-08-25T16:21:59
2026-08-25T16:22:04
2026-08-25T16:22:10
2026-08-25T16:22:15
2026-08-25T16:22:20
2026-08-25T16:22:26
2026-08-25T16:22:31
2026-08-25T16:22:36
2026-08-25T16:25:04 | 114.31 | 298.2
2026-08-25T16:25:09 | 114.31 | 298.2
2026-08-25T16:25:15 | 114.5 | 298.2
2026-08-25T16:25:20 | 114.5 | 298.2
2026-08-25T16:25:25 | 114.5 | 298.2
2026-08-25T16:25:30 | 114.43 | 298.2
2026-08-25T16:25:35 | 114.62 | 298.2
2026-08-25T16:25:40 | 114.62 | 298.2
2026-08-25T16:25:45 | 114.5 | 298.2
2026-08-25T16:25:50 | 114.5 | 298.2
2026-08-25T16:25:55 | 114.5 | 298.2
2026-08-25T16:26:00 | 114.5 | 298.2
2026-08-25T16:26:05 | 114.39 | 298.2
2026-08-25T16:26:10 | 114.39 | 298.2
2026-08-25T16:26:15 | 114.39 | 298.2
2026-08-25T16:26:20 | 114.2 | 298.2
2026-08-25T16:26:26 | 114.39 | 298.2
2026-08-25T16:26:31 | 114.39 | 298.2
2026-08-25T16:26:36 | 114.39 | 298.2
2026-08-25T16:26:41 | 114.39 | 298.2
2026-08-25T16:26:46 | 114.5 | 298.2
2026-08-25T16:26:51 | 114.31 | 298.2
2026-08-25T16:26:56 | 114.39 | 298.2
2026-08-25T16:27:01 | 114.31 | 298.2
2026-08-25T16:27:06 | 114.5 | 298.2
2026-08-25T16:27:11 | 114.39 | 298.2
2026-08-25T16:27:16 | 114.39 | 298.2
2026-08-25T16:27:21 | 114.39 | 298.2
2026-08-25T16:27:26 | 114.39 | 298.2
2026-08-25T16:27:31 | 114.5 | 298.2
2026-08-25T16:27:37 | 114.39 | 298.2
2026-08-25T16:27:42 | 114.57 | 298.2
2026-08-25T16:27:47 | 114.57 | 298.2
2026-08-25T16:27:52 | 114.57 | 298.2
2026-08-25T16:27:57 | 114.57 | 298.2
2026-08-25T16:28:02 | 114.57 | 298.2
2026-08-25T16:28:07 | 114.57 | 298.2
2026-08-25T16:28:12 | 114.39 | 298.2
2026-08-25T16:28:17 | 114.57 | 298.2
2026-08-25T16:28:22 | 114.57 | 298.2
2026-08-25T16:28:27 | 114.57 | 298.2
2026-08-25T16:28:32 | 114.46 | 298.2
2026-08-25T16:28:37 | 114.53 | 298.2
2026-08-25T16:28:42 | 114.64 | 298.2
2026-08-25T16:28:47 | 114.46 | 298.2
2026-08-25T16:28:53 | 114.46 | 298.2
2026-08-25T16:28:58 | 114.57 | 298.2
2026-08-25T16:29:03 | 114.57 | 298.2
2026-08-25T16:29:08 | 114.57 | 298.2
2026-08-25T16:29:13 | 114.57 | 298.2
2026-08-25T16:29:18 | 114.46 | 298.2
2026-08-25T16:29:23 | 114.46 | 298.2
2026-08-25T16:29:28 | 114.57 | 298.2
2026-08-25T16:29:33 | 114.39 | 298.2
2026-08-25T16:29:38 | 114.39 | 298.2
2026-08-25T16:29:43 | 114.39 | 298.2
2026-08-25T16:29:48 | 114.46 | 298.2
2026-08-25T16:29:53 | 114.34 | 298.2
2026-08-25T16:29:58 | 114.46 | 298.2
2026-08-25T16:30:04 | 114.46 | 298.2
2026-08-25T16:34:07 |  | 145.93
2026-08-25T16:34:13 |  | 145.93
2026-08-25T16:34:19 |  | 145.93
2026-08-25T16:34:24 |  | 145.93
2026-08-25T16:34:30 |  | 145.93
2026-08-25T16:34:36 |  | 145.93
2026-08-25T16:34:42 |  | 145.93
2026-08-25T16:34:47 |  | 145.93
2026-08-25T16:34:52 |  | 145.93
2026-08-25T16:34:58 |  | 145.93
2026-08-25T16:35:04 |  | 145.93
2026-08-25T16:35:09 |  | 145.93
2026-08-25T16:35:15 |  | 145.33
2026-08-25T16:35:20 |  | 145.33
2026-08-25T16:35:25 |  | 145.33
2026-08-25T16:35:31 |  | 144.73
2026-08-25T16:35:36 |  | 144.73
2026-08-25T16:35:42 |  | 144.73
2026-08-25T16:35:47 |  | 144.73
2026-08-25T16:35:53 |  | 144.73
2026-08-25T16:35:58 |  | 144.73
2026-08-25T16:36:05 |  | 145.33
2026-08-25T16:36:10 |  | 145.33
2026-08-25T16:36:16 |  | 145.33
2026-08-25T16:36:21 |  | 145.33
2026-08-25T16:36:27 |  | 145.33
2026-08-25T16:36:32 |  | 145.33
2026-08-25T16:36:38 |  | 145.33
2026-08-25T16:36:43 |  | 145.33
2026-08-25T16:36:49 |  | 145.33
2026-08-25T16:36:54 |  | 145.33
2026-08-25T16:37:01 |  | 145.33
2026-08-25T16:37:06 |  | 145.33
2026-08-25T16:37:12 |  | 145.33
2026-08-25T16:37:17 |  | 145.33
2026-08-25T16:37:23 |  | 145.33
2026-08-25T16:37:28 |  | 145.33
2026-08-25T16:37:34 |  | 145.33
2026-08-25T16:37:40 |  | 145.33
2026-08-25T16:37:46 |  | 145.33
2026-08-25T16:37:51 |  | 145.33
2026-08-25T16:37:58 |  | 145.33
2026-08-25T16:38:03 |  | 145.33
2026-08-25T16:38:09 |  | 145.33
2026-08-25T16:38:17 | 191.78 | 114.34
2026-08-25T16:38:22 | 191.78 | 114.34
2026-08-25T16:38:27 | 191.78 | 114.34
2026-08-25T16:38:32 | 191.78 | 114.34
2026-08-25T16:38:38 | 191.78 | 114.34
2026-08-25T16:38:43 | 191.78 | 114.27
2026-08-25T16:38:48 | 191.78 | 114.46
2026-08-25T16:38:53 | 191.78 | 114.34
2026-08-25T16:38:58 | 191.78 | 114.46
2026-08-25T16:39:03 | 191.78 | 114.46
2026-08-25T16:39:08 | 191.78 | 114.46
2026-08-25T16:39:13 | 191.78 | 114.46
2026-08-25T16:39:18 | 191.78 | 114.46
2026-08-25T16:39:23 | 191.78 | 114.46
2026-08-25T16:39:28 | 191.78 | 114.46
2026-08-25T16:39:33 | 191.78 | 114.34
2026-08-25T16:39:38 | 191.78 | 114.46
2026-08-25T16:39:43 | 191.78 | 114.46
2026-08-25T16:39:48 | 191.78 | 114.27
2026-08-25T16:39:53 | 191.78 | 114.27
2026-08-25T16:39:58 | 191.78 | 114.39
2026-08-25T16:40:04 | 191.78 | 114.2
2026-08-25T16:40:09 | 191.78 | 114.2
2026-08-25T16:40:14 | 191.78 | 114.2
2026-08-25T16:40:19 | 191.78 | 114.39
2026-08-25T16:40:24 | 191.78 | 114.39
2026-08-25T16:40:29 | 191.78 | 114.2
2026-08-25T16:40:34 | 191.78 | 114.2
2026-08-25T16:40:39 | 191.78 | 114.2
2026-08-25T16:40:44 | 191.78 | 114.2
2026-08-25T16:40:49 | 191.78 | 114.2
2026-08-25T16:40:54 | 191.78 | 114.2
2026-08-25T16:40:59 | 191.78 | 114.2
2026-08-25T16:41:04 | 191.78 | 114.2
2026-08-25T16:41:09 | 191.78 | 114.2
2026-08-25T16:41:14 | 191.78 | 114.2
2026-08-25T16:41:19 | 191.78 | 114.2
2026-08-25T16:41:24 | 191.78 | 114.2
2026-08-25T16:41:30 | 191.78 | 114.2
2026-08-25T16:41:35 | 191.78 | 114.2
2026-08-25T16:41:40 | 191.78 | 114.2
2026-08-25T16:41:45 | 191.78 | 114.2
2026-08-25T16:41:50 | 191.78 | 114.39
2026-08-25T16:41:55 | 191.78 | 114.39
2026-08-25T16:42:00 | 191.78 | 114.2
2026-08-25T16:42:05 | 191.78 | 114.2
2026-08-25T16:42:10 | 191.78 | 114.2
2026-08-25T16:42:15 | 191.78 | 114.2
2026-08-25T16:42:20 | 191.78 | 114.62
2026-08-25T16:42:25 | 191.78 | 114.2
2026-08-25T16:42:30 | 191.78 | 114.2
2026-08-25T16:42:35 | 191.78 | 114.2
2026-08-25T16:42:42 | 191.78
2026-08-25T16:42:47 | 191.78
2026-08-25T16:42:52 | 191.78
2026-08-25T16:42:57 | 191.78
2026-08-25T16:43:02 | 191.78
2026-08-25T16:43:07 | 191.78
2026-08-25T16:43:12 | 191.78
2026-08-25T16:43:17 | 191.78
2026-08-25T16:43:22 | 191.78
2026-08-25T16:43:27 | 191.78
2026-08-25T16:43:31
2026-08-25T16:43:36
2026-08-25T16:43:41
2026-08-25T16:43:46
2026-08-25T16:43:50
2026-08-25T16:43:55
2026-08-25T16:44:00
2026-08-25T16:44:05
2026-08-25T16:44:10
2026-08-25T16:44:15
2026-08-25T16:44:20
2026-08-25T16:44:25
2026-08-25T16:44:36 | 0.22
2026-08-25T16:44:41 | 0.22
2026-08-25T16:44:46 | 0.22
2026-08-25T16:44:51 | 0.22
2026-08-25T16:44:56 | 0.22
2026-08-25T16:45:00 | 0.22
2026-08-25T16:45:05 | 0
2026-08-25T16:45:10 | 0.22
2026-08-25T16:45:15 | 0
2026-08-25T16:45:20 | 0
2026-08-25T16:45:25 | 0
2026-08-25T16:45:32 | 0
2026-08-25T16:45:37 | 0.22
2026-08-25T16:45:42 | 0.22
2026-08-25T16:45:47 | 0.44
2026-08-25T16:45:52 | 0.22 | 0
2026-08-25T16:45:57 | 0.22 | 0
2026-08-25T16:46:02 | 0.22 | 0
2026-08-25T16:46:07 | 0.22 | 0
2026-08-25T16:46:13 | 0.44 | 0
2026-08-25T16:46:17 | 0.22 | 0
2026-08-25T16:46:22 | 0.44 | 0
2026-08-25T16:46:27 | 0.44 | 0
2026-08-25T16:46:33 | 0.44 | 0
2026-08-25T16:46:38 | 0.44 | 0
2026-08-25T16:46:43 | 0.44 | 0
2026-08-25T16:46:48 | 0.44 | 0
2026-08-25T16:46:53 | 0.44 | 0
2026-08-25T16:46:58 | 0.22 | 0
2026-08-25T16:47:03 | 0.22 | 0
2026-08-25T16:47:08 | 0.44 | 0
2026-08-25T16:47:13 | 0.22 | 0
2026-08-25T16:47:18 | 0.44 | 0
2026-08-25T16:47:23 | 0.22 | 0
2026-08-25T16:47:28 | 0.22 | 0
2026-08-25T16:47:33 | 0.22 | 0
2026-08-25T16:47:38 | 0.22 | 0
2026-08-25T16:47:43 | 0.44 | 0
2026-08-25T16:47:48 | 0.22 | 0
2026-08-25T16:47:53 | 0 | 0
2026-08-25T16:47:58 | 0 | 0
2026-08-25T16:48:03 | 0 | 0
2026-08-25T16:48:09 | 0.22 | 0
2026-08-25T16:48:14 | 0.22 | 0
2026-08-25T16:48:19 | 0 | 0
2026-08-25T16:48:24 | 0.22 | 0
2026-08-25T16:48:29 | 0.44 | 0
2026-08-25T16:48:34 | 0 | 0
2026-08-25T16:48:39 | 0.22 | 0
2026-08-25T16:48:44 | 0.22 | 0
2026-08-25T16:48:49 | 0.44 | 0
2026-08-25T16:48:54 | 0.22 | 0
2026-08-25T16:48:59 | 0.44 | 0
2026-08-25T16:49:04 | 0.44 | 0
2026-08-25T16:49:09 | 0.22 | 0
2026-08-25T16:49:14 | 0.43 | 0
2026-08-25T16:49:19 | 0.43 | 0
2026-08-25T16:49:24 | 0.43 | 0
2026-08-25T16:49:29 | 0.65 | 0
2026-08-25T16:49:34 | 0.43 | 0
2026-08-25T16:49:40 | 0.43 | 0
2026-08-25T16:49:45 | 0.22 | 0
2026-08-25T16:49:50 | 0.22 | 0
2026-08-25T16:49:55 | 0.22 | 0
2026-08-25T16:50:00 | 0.43 | 0
2026-08-25T16:50:05 | 0.43 | 0
2026-08-25T16:50:10 | 0.44 | 0
2026-08-25T16:50:15 | 0.44 | 0
2026-08-25T16:50:20 | 0.44 | 0
2026-08-25T16:50:25 | 0.44 | 0
2026-08-25T16:50:30 | 0.44 | 0
2026-08-25T16:50:35 | 0.44 | 0
2026-08-25T16:50:40 | 0.44 | 0
2026-08-25T16:50:45 | 0.43 | 0
2026-08-25T16:50:50 | 0.44 | 0
2026-08-25T16:50:55 | 0.22 | 0
2026-08-25T16:51:00 | 0.44 | 0
2026-08-25T16:51:05 | 0.44 | 0
2026-08-25T16:51:11 | 0.44 | 0
2026-08-25T16:51:16 | 0.22 | 0
2026-08-25T16:51:21 | 0.44 | 0
2026-08-25T16:51:26 | 0.22 | 0
2026-08-25T16:51:31 | 0.44 | 0
2026-08-25T16:51:36 | 0.44 | 0
2026-08-25T16:51:41 | 0.22 | 0
2026-08-25T16:51:46 | 0.22 | 0
2026-08-25T16:51:51 | 0.44 | 0
2026-08-25T16:51:56 | 0.22 | 0
2026-08-25T16:52:01 | 0.22 | 0
2026-08-25T16:52:06 | 0.22 | 0
2026-08-25T16:52:11 | 0.22 | 0
2026-08-25T16:52:16 | 0 | 0
2026-08-25T16:52:21 | 0.22 | 0
2026-08-25T16:52:26 | 0.22 | 0
2026-08-25T16:52:31 | 0.22 | 0
2026-08-25T16:52:36 | 0.44 | 0
2026-08-25T16:52:42 | 0.44 | 0
2026-08-25T16:52:47 | 0.44 | 0
2026-08-25T16:52:52 | 0.44 | 0
2026-08-25T16:52:57 | 0.44 | 0
2026-08-25T16:53:02 | 0.44 | 0
2026-08-25T16:53:07 | 0.22 | 0
2026-08-25T16:53:12 | 0.44 | 0
2026-08-25T16:53:17 | 0.44 | 0
2026-08-25T16:53:22 | 0.44 | 0
2026-08-25T16:53:27 | 0.44 | 0
2026-08-25T16:53:32 | 0.44 | 0
2026-08-25T16:53:37 | 0.22 | 0
2026-08-25T16:53:42 | 0.22 | 0
2026-08-25T16:53:47 | 0.22 | 0
2026-08-25T16:53:52 | 0.22 | 0
2026-08-25T16:53:57 | 0.22 | 0
2026-08-25T16:54:02 | 0.22 | 0
2026-08-25T16:54:08 |  | 145.33
2026-08-25T16:54:14 |  | 145.33
2026-08-25T16:54:20 |  | 145.33
2026-08-25T16:54:26 |  | 145.33
2026-08-25T16:54:33 |  | 145.33
2026-08-25T16:54:38 |  | 145.33
2026-08-25T16:54:44 |  | 145.33
2026-08-25T16:54:50 |  | 145.33
2026-08-25T16:54:56 |  | 145.33
2026-08-25T16:55:02 |  | 145.33
2026-08-25T16:55:08 |  | 145.33
2026-08-25T16:55:15 |  | 145.33
2026-08-25T16:55:20 |  | 145.33
2026-08-25T16:55:27 |  | 145.33
2026-08-25T16:55:33 |  | 145.33
2026-08-25T16:55:39 |  | 145.33
2026-08-25T16:55:45 |  | 145.33
2026-08-25T16:55:51 |  | 145.33
2026-08-25T16:55:57 |  | 145.33
2026-08-25T16:56:04 |  | 145.33
2026-08-25T16:56:29 | 0.22 | 0
2026-08-25T16:56:35 | 0.43 | 0
2026-08-25T16:56:40 | 0.44 | 0
2026-08-25T16:56:46 | 0.22 | 0
2026-08-25T16:56:51 | 0.22 | 0
2026-08-25T16:56:56 | 0.22 | 0
2026-08-25T16:57:03 | 0.43 | 0
2026-08-25T16:57:09 | 0.43 | 0
2026-08-25T16:57:14 | 0.65 | 0
2026-08-25T16:57:19 | 0.65 | 0
2026-08-25T16:57:24 | 0.65 | 0
2026-08-25T16:57:30 | 0.44 | 0
2026-08-25T16:57:35 | 0.44 | 0
2026-08-25T16:57:40 | 0.44 | 0
2026-08-25T16:57:45 | 0.44 | 0
2026-08-25T16:57:50 | 0.43 | 0
2026-08-25T16:57:56 | 0.43 | 1.26
2026-08-25T16:58:01 | 0.22 | 1.26
2026-08-25T16:58:06 | 0.22 | 1.26
2026-08-25T16:58:11 | 0 | 1.26
2026-08-25T16:58:16 | 0.22 | 1.26
2026-08-25T16:58:21 | 7.42 | 0
2026-08-25T16:58:29 | 0 | 0
2026-08-25T16:58:34 | 2.71 | 0
2026-08-25T16:58:39
2026-08-25T17:01:33 | 0.23
2026-08-25T17:01:38 | 0.23
2026-08-25T17:01:43 | 0.68
2026-08-25T17:01:48 | 0.45
2026-08-25T17:01:53 | 0.45
2026-08-25T17:01:58 | 0.68
2026-08-25T17:02:03 | 0.23
2026-08-25T17:02:08 | 0.45
2026-08-25T17:02:13 | 0.68
2026-08-25T17:02:18 | 0.23
2026-08-25T17:02:23 | 0.45
2026-08-25T17:02:28 | 0.23
2026-08-25T17:02:34 | 0.23
2026-08-25T17:02:39 | 0.45
2026-08-25T17:02:44 | 0.45
2026-08-25T17:02:49 | 0.45
2026-08-25T17:02:54 | 0.45
2026-08-25T17:02:59 | 0.45
2026-08-25T17:03:04 | 0.23
2026-08-25T17:03:09 | 0.23
2026-08-25T17:03:14 | 0.23
2026-08-25T17:03:19 | 0
2026-08-25T17:03:24 | 0
2026-08-25T17:03:29 | 0.23
2026-08-25T17:03:34 | 0.23
2026-08-25T17:03:39 | 0.23
2026-08-25T17:44:04 | 0
2026-08-25T17:44:10 | 0
2026-08-25T17:44:16 | 0
2026-08-25T17:44:21 | 0.23
2026-08-25T17:44:26 | 0
2026-08-25T17:44:31 | 0
2026-08-25T17:44:36 | 0.23
2026-08-25T17:44:41
2026-08-25T17:44:46
2026-08-25T17:44:52
2026-08-25T17:44:57
2026-08-25T17:45:02
2026-08-25T17:45:08
2026-08-25T17:45:13
2026-08-25T17:45:18
2026-08-25T17:45:24
2026-08-25T17:45:29
2026-08-25T17:45:34
2026-08-25T17:45:40
2026-08-25T17:45:45
2026-08-25T17:45:50
2026-08-25T17:45:56
2026-08-25T17:46:01
2026-08-25T17:46:06
2026-08-25T17:46:12
2026-08-25T17:46:17
2026-08-25T17:46:22
2026-08-25T17:46:29 | 0.23
2026-08-25T17:46:34 | 0.23
2026-08-25T17:46:39 | 0.23
2026-08-25T17:46:44 | 0.23
2026-08-25T17:46:49 | 0.23
2026-08-25T17:46:54 | 0.46
2026-08-25T17:46:59 | 0.23
2026-08-25T17:47:04 | 0.46
2026-08-25T17:47:09 | 0.23
2026-08-25T17:47:15 | 0.46
2026-08-25T17:47:20 | 0.46
2026-08-25T17:47:25 | 0.23
2026-08-25T17:47:30 | 0.23 | 0
2026-08-25T17:47:35 | 9.47 | 1.33
2026-08-25T17:47:40 | 8.99 | 1.32
2026-08-25T17:47:45 | 8.98 | 1.32
2026-08-25T17:47:50 | 17.57 | 1.33
2026-08-25T17:47:55 | 17.83 | 1.32
2026-08-25T17:48:00 | 17.57 | 1.32
2026-08-25T17:48:06 | 17.57 | 1.32
2026-08-25T17:48:11 | 0 | 0.74
2026-08-25T17:48:16 | 0 | 0.52
2026-08-25T17:48:21
2026-08-25T17:48:32 | 0.23 | 0.49
2026-08-25T17:48:35 | 0 | 0
2026-08-25T17:48:40 | 0.46 | 0.51
2026-08-25T17:48:45 | 0.23 | 0.51
2026-08-25T17:48:50 | 0.23 | 0.53
2026-08-25T17:48:55 | 0.23 | 0
2026-08-25T17:49:00 | 0.46 | 0
2026-08-25T17:49:05 | 0.46 | 0
2026-08-25T17:49:10 | 0.46 | 0
2026-08-25T17:49:15 | 0.23 | 0
2026-08-25T17:49:21 | 0.46 | 0
2026-08-25T17:49:26 | 0.46 | 0
2026-08-25T17:49:31 | 0.23 | 0
2026-08-25T17:49:36 | 0.46 | 0
2026-08-25T17:49:42 | 0.23 | 0
2026-08-25T17:49:47 | 0.46 | 0
2026-08-25T17:49:52 | 0.46 | 0
2026-08-25T17:49:57 | 0.46 | 0
2026-08-25T17:50:02 | 0.46 | 0
2026-08-25T17:50:07 | 0.46 | 0
2026-08-25T17:50:13 | 0.46 | 0
2026-08-25T17:50:19 | 0.46 | 0
2026-08-25T17:50:24 | 0.46 | 0
2026-08-25T17:50:29 | 0.46 | 0
2026-08-25T17:50:34 | 0.46 | 0
2026-08-25T17:50:39 | 0.23 | 0
2026-08-25T17:50:44 | 0.23 | 0
2026-08-25T17:50:49 | 0.23 | 0
2026-08-25T17:50:54 | 0.46 | 0
2026-08-25T17:50:59 | 0.46 | 0
2026-08-25T17:51:05 | 0.23 | 0
2026-08-25T17:51:10 | 0.46 | 0
2026-08-25T17:51:15 | 0.46 | 0
2026-08-25T17:51:20 | 0.46 | 0
2026-08-25T17:51:25 | 0.23 | 0
2026-08-25T17:51:30 | 0.46 | 0
2026-08-25T17:51:35 | 0.23 | 0
2026-08-25T17:51:40 | 0.46 | 0
2026-08-25T17:51:45 | 0.23 | 0
2026-08-25T17:51:50 | 0.23 | 0
2026-08-25T17:51:56 | 0.23 | 0
2026-08-25T17:52:01 | 0.23 | 0
2026-08-25T17:52:06 | 0.46 | 0
2026-08-25T17:52:11 | 0.46 | 0
2026-08-25T17:52:16 | 0.23 | 0
2026-08-25T17:52:21 | 0.23 | 0
2026-08-25T17:52:26 | 0.23 | 0
2026-08-25T17:52:32 | 0.23 | 0
2026-08-25T17:52:37 | 0.23 | 0
2026-08-25T17:52:42 | 0.23 | 0
2026-08-25T17:52:47 | 0.23 | 0
2026-08-25T17:52:53 | 0.23 | 0
2026-08-25T17:52:58 | 0.23 | 0
2026-08-25T17:53:03 | 0.23 | 0
2026-08-25T17:53:08 | 0.23 | 0
2026-08-25T17:53:13 | 0.23 | 0
2026-08-25T17:53:18 | 0.23 | 0
2026-08-25T17:53:23 | 0.45 | 0
2026-08-25T17:53:28 | 0.45 | 0
2026-08-25T17:53:33 | 0.23 | 0
2026-08-25T17:53:38 | 0.23 | 0
2026-08-25T17:53:44 | 0.46 | 0
2026-08-25T17:53:49 | 0.46 | 0
2026-08-25T17:53:56 | 0.45 | 0
2026-08-25T17:54:01 | 0.23 | 0
2026-08-25T17:54:06 | 0.46 | 0
2026-08-25T17:54:11 | 0.23 | 0
2026-08-25T17:54:16 | 0.23 | 0
2026-08-25T17:54:21 | 0.46 | 0
2026-08-25T17:54:26 | 0.23 | 0
2026-08-25T17:54:32 | 0.23 | 0
2026-08-25T17:54:37 | 0.23 | 0
2026-08-25T17:54:42 | 0.46 | 0
2026-08-25T17:54:47 | 0.46 | 0
2026-08-25T17:54:52 | 0.46 | 0
2026-08-25T17:54:57 | 0.46 | 0
2026-08-25T17:55:02 | 0.46 | 0
2026-08-25T17:55:07 | 0.46 | 0
2026-08-25T17:55:12 | 0.45 | 0
2026-08-25T17:55:17 | 0.23 | 0
2026-08-25T17:55:23 | 0.46 | 0
2026-08-25T17:55:28 | 0.23 | 0
2026-08-25T17:55:33 | 0.23 | 0
2026-08-25T17:55:39 | 0.23 | 0
2026-08-25T17:55:44 | 0.23 | 0
2026-08-25T17:55:49 | 0.23 | 0
2026-08-25T17:55:54 | 0.23 | 0
2026-08-25T17:55:59 | 0.23 | 0
2026-08-25T17:56:04 | 0.23 | 0
2026-08-25T17:56:09 | 0 | 0
2026-08-25T17:56:14 | 0.23 | 0
2026-08-25T17:56:20 | 0.23 | 0
2026-08-25T17:56:25 | 0.23 | 0
2026-08-25T17:56:30 | 0.45 | 0
2026-08-25T17:56:35 | 0.23 | 0
2026-08-25T17:56:40 | 0.23 | 0
2026-08-25T17:56:45 | 0.23 | 0
2026-08-25T17:56:50 | 0.23 | 0
2026-08-25T17:56:55 | 0.23 | 0
2026-08-25T17:57:00 | 0.23 | 0
2026-08-25T17:57:05 | 0.23 | 0
2026-08-25T17:57:11 | 0.23 | 0
2026-08-25T17:57:16 | 0.23 | 0
2026-08-25T17:57:21 | 0.45 | 0
2026-08-25T17:57:26 | 0.23 | 0
2026-08-25T17:57:31 | 0.23 | 0
2026-08-25T17:57:36 | 0.23 | 0
2026-08-25T17:57:41 | 0.45 | 0
2026-08-25T17:57:46 | 0.68 | 0
2026-08-25T17:57:51 | 0.45 | 0
2026-08-25T17:57:57 | 0.45 | 0
2026-08-25T17:58:03 | 0.23 | 0
2026-08-25T17:58:08 | 0.23 | 0
2026-08-25T17:58:13 | 0 | 0
2026-08-25T17:58:18 | 0 | 0
2026-08-25T17:58:23 | 0 | 0
2026-08-25T17:58:28 | 0 | 0
2026-08-25T17:58:33 | 0.23 | 0
2026-08-25T17:58:38 | 0 | 0
2026-08-25T17:58:43 | 0 | 0
2026-08-25T17:58:48 | 0 | 0
2026-08-25T17:58:54 | 0 | 0
2026-08-25T17:58:59 | 0 | 0
2026-08-25T17:59:04 | 0 | 0
2026-08-25T17:59:09 | 0.23 | 0
2026-08-25T17:59:14 | 0.23 | 0
2026-08-25T17:59:19 | 0.23 | 0
2026-08-25T17:59:24 | 0.23 | 0
2026-08-25T17:59:29 | 0.23 | 0
2026-08-25T17:59:34 | 0.23 | 0
2026-08-25T17:59:39 | 0 | 0
2026-08-25T17:59:44 | 0.23 | 0
2026-08-25T17:59:50 | 0.23 | 0
2026-08-25T17:59:55 | 0.23 | 0
2026-08-25T18:00:00 | 0.23 | 0
2026-08-25T18:00:05 | 0.23 | 0
2026-08-25T18:00:11 | 0.23 | 0
2026-08-25T18:00:16 | 0.23 | 0
2026-08-25T18:00:21 | 0.45 | 0
2026-08-25T18:00:26 | 0.45 | 0
2026-08-25T18:00:31 | 0.45 | 0
2026-08-25T18:00:36 | 0.45 | 0
2026-08-25T18:00:42 | 0.45 | 0
2026-08-25T18:00:47 | 0.23 | 0
2026-08-25T18:00:52 | 0.23 | 0
2026-08-25T18:00:57 | 0.23 | 0
2026-08-25T18:01:02 | 0.23 | 0
2026-08-25T18:01:07 | 0 | 0
2026-08-25T18:01:12 | 0 | 0
2026-08-25T18:01:17 | 0 | 0
2026-08-25T18:01:22 | 0 | 0
2026-08-25T18:01:27 | 0.23 | 0
2026-08-25T18:01:33 | 0.23 | 0
2026-08-25T18:01:38 | 0.23 | 0
2026-08-25T18:01:43 | 0.23 | 0
2026-08-25T18:01:48 | 0.45 | 0
2026-08-25T18:01:53 | 0.23 | 0
2026-08-25T18:01:58 | 0.23 | 0
2026-08-25T18:02:03 | 0 | 0
2026-08-25T18:02:08 | 0.23 | 0
2026-08-25T18:02:13 | 0.23 | 0
2026-08-25T18:02:18 | 0 | 0
2026-08-25T18:02:23 | 0.23 | 0
2026-08-25T18:02:29 | 0.45 | 0
2026-08-25T18:02:34 | 0.45 | 0
2026-08-25T18:02:39 | 0.45 | 0
2026-08-25T18:02:44 | 0.23 | 0
2026-08-25T18:02:49 | 0.23 | 0
2026-08-25T18:02:54 | 0.45 | 0
2026-08-25T18:02:59 | 0.23 | 0
2026-08-25T18:03:04 | 0.23 | 0
2026-08-25T18:03:09 | 0.23 | 0
2026-08-25T18:03:14 | 0.23 | 0
2026-08-25T18:03:20 | 0.45 | 0
2026-08-25T18:03:25 | 0.23 | 0
2026-08-25T18:03:30 | 0.23 | 0
2026-08-25T18:03:35 | 0.23 | 0
2026-08-25T18:03:40 | 0.23 | 0
2026-08-25T18:03:45 | 0.46 | 0
2026-08-25T18:03:50 | 0.23 | 0
2026-08-25T18:03:55 | 0.23 | 0
2026-08-25T18:04:00 | 0 | 0
2026-08-25T18:04:06 | 0.46 | 0
2026-08-25T18:04:11 | 0 | 2.73
2026-08-25T18:04:16 | 0.23 | 0
2026-08-25T18:04:22 | 0.23 | 0
2026-08-25T18:04:28 | 0.23 | 0
2026-08-25T18:04:33 | 0.23 | 0
2026-08-25T18:04:38 | 0.46 | 0
2026-08-25T18:04:43 | 0.46 | 2.75
2026-08-25T18:04:48 | 0.46 | 2.75
2026-08-25T18:04:54 | 0.46 | 2.75
2026-08-25T18:04:59 | 0.46 | 2.75
2026-08-25T18:05:04 | 0.46 | 2.75
2026-08-25T18:05:09 | 0.23 | 2.73
2026-08-25T18:05:14 | 0.46 | 2.73
2026-08-25T18:05:19 | 0.46 | 2.73
2026-08-25T18:05:24 | 0.46 | 2.73
2026-08-25T18:05:29 | 0.46 | 2.75
2026-08-25T18:05:34 | 0.46 | 2.75
2026-08-25T18:05:39 | 0.23 | 2.75
2026-08-25T18:05:45 | 0.23 | 2.75
2026-08-25T18:05:50 | 0.46 | 2.75
2026-08-25T18:05:55 | 0.23 | 2.75
2026-08-25T18:06:00 | 0.23 | 0
2026-08-25T18:06:05 | 0.23 | 0
2026-08-25T18:06:11 | 0.23 | 2.75
2026-08-25T18:06:16 | 0.46 | 2.75
2026-08-25T18:06:21
2026-08-25T18:06:26
2026-08-25T18:06:31
2026-08-25T18:06:37
2026-08-25T18:06:42
2026-08-25T18:06:47
2026-08-25T18:06:53
2026-08-25T18:06:58
2026-08-25T18:07:03
2026-08-25T18:07:04
2026-08-25T18:07:09
2026-08-25T18:07:11
2026-08-25T18:07:14
2026-08-25T18:07:17
2026-08-25T18:07:19
2026-08-25T18:07:22
2026-08-25T18:07:25
2026-08-25T18:07:27
2026-08-25T18:07:30
2026-08-25T18:07:33
2026-08-25T18:07:35
2026-08-25T18:07:38
2026-08-25T18:07:41
2026-08-25T18:07:43
2026-08-25T18:07:46
2026-08-25T18:07:49
2026-08-25T18:07:51
2026-08-25T18:07:54
2026-08-25T18:07:57
2026-08-25T18:07:59
2026-08-25T18:08:02
2026-08-25T18:08:05
2026-08-25T18:08:07
2026-08-25T18:08:10
2026-08-25T18:08:13
2026-08-25T18:08:15
2026-08-25T18:08:18
2026-08-25T18:08:21
2026-08-25T18:08:23
2026-08-25T18:08:26
2026-08-25T18:08:28
2026-08-25T18:08:31
2026-08-25T18:08:34
2026-08-25T18:08:36
2026-08-25T18:08:39
2026-08-25T18:08:42
2026-08-25T18:08:44
2026-08-25T18:08:47
2026-08-25T18:08:50
2026-08-25T18:08:52
2026-08-25T18:08:55
2026-08-25T18:08:58
2026-08-25T18:09:00
2026-08-25T18:09:03
2026-08-25T18:09:06
2026-08-25T18:09:08
2026-08-25T18:09:11
2026-08-25T18:09:14
2026-08-25T18:09:16
2026-08-25T18:09:19
2026-08-25T18:09:22
2026-08-25T18:09:24
2026-08-25T18:09:27
2026-08-25T18:09:30
2026-08-25T18:09:32
2026-08-25T18:09:35
2026-08-25T18:09:38
2026-08-25T18:09:40
2026-08-25T18:09:43
2026-08-25T18:09:46
2026-08-25T18:09:47 | 0.23 | 0
2026-08-25T18:09:51
2026-08-25T18:09:52 | 0.23 | 0
2026-08-25T18:09:56
2026-08-25T18:09:57 | 0.46 | 0
2026-08-25T18:10:02
2026-08-25T18:10:02 | 0.23 | 0
2026-08-25T18:10:07
2026-08-25T18:10:07 | 0.23 | 0
2026-08-25T18:10:12
2026-08-25T18:10:12 | 0.46 | 0
2026-08-25T18:10:17
2026-08-25T18:10:18
2026-08-25T18:10:23
2026-08-25T18:10:23
2026-08-25T18:10:28
2026-08-25T18:10:28
2026-08-25T18:10:33 | 0.46 | 0
2026-08-25T18:10:33
2026-08-25T18:10:38 | 0.23 | 0
2026-08-25T18:10:39
2026-08-25T18:10:43 | 0 | 0
2026-08-25T18:10:44
2026-08-25T18:10:48 | 0 | 0
2026-08-25T18:10:49
2026-08-25T18:10:53 | 0 | 0
2026-08-25T18:10:55
2026-08-25T18:10:58 | 0 | 0
2026-08-25T18:11:00
2026-08-25T18:11:03 | 0.23 | 0
2026-08-25T18:11:05
2026-08-25T18:11:08 | 0.23 | 0
2026-08-25T18:11:11
2026-08-25T18:11:14 | 0.23 | 0
2026-08-25T18:11:16
2026-08-25T18:11:19 | 0.23 | 0
2026-08-25T18:11:21
2026-08-25T18:11:24 | 0.46 | 0
2026-08-25T18:11:27
2026-08-25T18:11:29 | 0.23 | 0
2026-08-25T18:11:32
2026-08-25T18:11:34 | 0.23 | 0
2026-08-25T18:11:37
2026-08-25T18:11:39 | 0.23 | 0
2026-08-25T18:11:43
2026-08-25T18:11:44 | 0.23 | 0
2026-08-25T18:11:48
2026-08-25T18:11:49 | 0 | 0
2026-08-25T18:11:53
2026-08-25T18:11:54 | 0.23 | 0
2026-08-25T18:11:58
2026-08-25T18:11:59 | 0.23 | 0
2026-08-25T18:12:04
2026-08-25T18:12:05 | 0.23 | 0
2026-08-25T18:12:09
2026-08-25T18:12:10 | 0.23 | 0
2026-08-25T18:12:14
2026-08-25T18:12:15 | 0 | 0
2026-08-25T18:12:20 | 0 | 0
2026-08-25T18:12:20
2026-08-25T18:12:25 | 0.23 | 0
2026-08-25T18:12:25
2026-08-25T18:12:30
2026-08-25T18:12:30 | 0 | 0
2026-08-25T18:12:36
2026-08-25T18:12:36 | 0.23 | 0
2026-08-25T18:12:41
2026-08-25T18:12:41 | 0 | 0
2026-08-25T18:12:46
2026-08-25T18:12:47 | 0 | 0
2026-08-25T18:12:52
2026-08-25T18:12:52 | 0 | 0
2026-08-25T18:12:57
2026-08-25T18:12:58 | 0 | 0
2026-08-25T18:13:02
2026-08-25T18:13:03 | 0 | 0
2026-08-25T18:13:08 | 0.23 | 0
2026-08-25T18:13:08
2026-08-25T18:13:13 | 0 | 0
2026-08-25T18:13:13
2026-08-25T18:13:18 | 0 | 0
2026-08-25T18:13:18
2026-08-25T18:13:23 | 0 | 0
2026-08-25T18:13:24
2026-08-25T18:13:28 | 0 | 0
2026-08-25T18:13:29
2026-08-25T18:13:33 | 0 | 0
2026-08-25T18:13:34
2026-08-25T18:13:38 | 0 | 0
2026-08-25T18:13:39
2026-08-25T18:13:43 | 0 | 0
2026-08-25T18:13:45
2026-08-25T18:13:50 | 0.23 | 0
2026-08-25T18:13:50
2026-08-25T18:13:55 | 0 | 0
2026-08-25T18:13:55
2026-08-25T18:14:00 | 0.23 | 0
2026-08-25T18:14:13 | 0.23 | 0
2026-08-25T18:14:18 | 0.23 | 0
2026-08-25T18:14:23 | 0.23 | 0
2026-08-25T18:14:29 | 0.23 | 0
2026-08-25T18:14:34 | 0.23 | 0
2026-08-25T18:14:39 | 0.23 | 0
2026-08-25T18:14:44 | 0.23 | 0
2026-08-25T18:14:49 | 0.23 | 0
2026-08-25T18:14:54 | 0.46 | 0
2026-08-25T18:14:59 | 0.46 | 2.73
2026-08-25T18:15:04 | 0.23 | 2.75
2026-08-25T18:15:09 | 0.23 | 2.75
2026-08-25T18:15:14 | 0.23 | 2.73
2026-08-25T18:15:20 | 0.46 | 0
2026-08-25T18:15:25 | 0.23 | 2.73
2026-08-25T18:15:30 | 0.23 | 0
2026-08-25T18:15:35 | 0.23 | 2.73
2026-08-25T18:15:40 | 0.23 | 2.73
2026-08-25T18:15:45 | 0 | 2.73
2026-08-25T18:15:50 | 0 | 2.75
2026-08-25T18:15:55 | 0.23 | 2.73
2026-08-25T18:16:00 | 0.23 | 2.73
2026-08-25T18:16:05 | 0.23 | 2.73
2026-08-25T18:16:10 | 0.23 | 0
2026-08-25T18:16:16 | 0.23 | 0
2026-08-25T18:16:21 | 0.23 | 0
2026-08-25T18:16:26 | 0.46 | 0
2026-08-25T18:16:31 | 0.46 | 0
2026-08-25T18:16:37 | 0.23 | 0
2026-08-25T18:16:42 | 0.23 | 0
2026-08-25T18:16:47 | 0 | 0
2026-08-25T18:16:52 | 0.23 | 0
2026-08-25T18:16:57 | 0.23 | 0
2026-08-25T18:17:03 | 0.23 | 0
2026-08-25T18:17:08 | 0.23 | 0
2026-08-25T18:17:13 | 0.23 | 0
2026-08-25T18:17:18 | 0.23 | 0
2026-08-25T18:17:23 | 0.23 | 0
2026-08-25T18:17:28 | 0.23 | 0
2026-08-25T18:17:33 | 0 | 0
2026-08-25T18:17:38 | 0.23 | 0
2026-08-25T18:17:43 | 0 | 0
2026-08-25T18:17:48 | 0 | 0
2026-08-25T18:17:54 | 0.23 | 0
2026-08-25T18:17:59 | 0 | 0
2026-08-25T18:18:04 | 0 | 0
2026-08-25T18:18:09 | 0 | 0
2026-08-25T18:18:14 | 0 | 0
2026-08-25T18:18:19 | 0 | 0
2026-08-25T18:18:24 | 0.23 | 0
2026-08-25T18:18:29 | 0.23 | 0
2026-08-25T18:18:34 | 0.23 | 0
2026-08-25T18:18:39 | 0 | 0
2026-08-25T18:18:45 | 0.23 | 0
2026-08-25T18:18:50 | 0.23 | 0
2026-08-25T18:18:55 | 0.23 | 0
2026-08-25T18:19:00 | 0.23 | 0
2026-08-25T18:19:05 | 0.23 | 0
2026-08-25T18:19:10 | 0.23 | 0
2026-08-25T18:19:15 | 0.45 | 0
2026-08-25T18:19:20 | 0.23 | 0
2026-08-25T18:19:25 | 0.23 | 0
2026-08-25T18:19:30 | 0 | 0
2026-08-25T18:19:36 | 0.23 | 0
2026-08-25T18:19:41 | 0 | 0
2026-08-25T18:19:46 | 0.23
2026-08-25T18:19:51 | 0.23 | 1.42
2026-08-25T18:19:56 | 0 | 0
2026-08-25T18:20:01 | 0
2026-08-25T18:20:06 | 0.23
2026-08-25T18:20:11 | 0.45
2026-08-25T18:20:16 | 0.45
2026-08-25T18:20:21 | 0.45
2026-08-25T18:20:26 | 0.45
2026-08-25T18:20:32 | 0.45 | 0
2026-08-25T18:20:37 | 0.45 | 0.74
2026-08-25T18:20:42 | 0.23 | 0
2026-08-25T18:20:47 | 0.23 | 0
2026-08-25T18:20:52 | 0.23 | 0
2026-08-25T18:20:57 | 0.45 | 0
2026-08-25T18:21:02 | 0.45 | 0
2026-08-25T18:21:07 | 0 | 0.74
2026-08-25T18:21:12 | 0.23 | 0.74
2026-08-25T18:21:17 | 0.45 | 0.74
2026-08-25T18:21:23 | 0.45 | 0.74
2026-08-25T18:21:28 | 0.45 | 0.74
2026-08-25T18:21:33 | 0.45 | 0
2026-08-25T18:21:38 | 0.45 | 0
2026-08-25T18:21:43 | 0.23 | 0
2026-08-25T18:21:48 | 0 | 0.74
2026-08-25T18:21:53 | 0.23 | 0.74
2026-08-25T18:21:58 | 0.23 | 0.74
2026-08-25T18:22:03 | 0.45 | 0.74
2026-08-25T18:22:08 | 0.23 | 0.74
2026-08-25T18:22:13 | 0.45 | 0.74
2026-08-25T18:22:19 | 0 | 0
2026-08-25T18:22:24 | 0.23 | 0
2026-08-25T18:22:29 | 0.23 | 0
2026-08-25T18:22:34 | 0.23 | 0
2026-08-25T18:22:41 | 0 | 0
2026-08-25T18:22:46 | 0.23 | 0
2026-08-25T18:22:52 | 0 | 0
2026-08-25T18:22:54 | 0 | 0
2026-08-25T18:22:59 | 0 | 0
2026-08-25T18:23:04 | 0 | 0.75
2026-08-25T18:23:10 | 0.23 | 0
2026-08-25T18:23:15 | 0.23 | 0.75
2026-08-25T18:23:20 | 0 | 0
2026-08-25T18:23:25 | 0 | 0
2026-08-25T18:23:30 | 0.23 | 0
2026-08-25T18:23:35 | 0 | 0.77
2026-08-25T18:23:40 | 0.23 | 0.77
2026-08-25T18:23:45 | 0.23 | 0.77
2026-08-25T18:23:50 | 0.23 | 0.77
2026-08-25T18:23:55 | 0.23 | 0.77
2026-08-25T18:24:01 | 0 | 0.77
2026-08-25T18:24:06 | 0.23 | 0.77
2026-08-25T18:24:11 | 0.23 | 0.77
2026-08-25T18:24:16 | 0.23 | 0.77
2026-08-25T18:24:21 | 0.45 | 0.77
2026-08-25T18:24:26 | 0.23 | 0.77
2026-08-25T18:24:31 | 0.45 | 0.77
2026-08-25T18:24:36 | 0.45 | 0.77
2026-08-25T18:24:41 | 0.45 | 0.77
2026-08-25T18:24:47 | 0.45 | 0.77
2026-08-25T18:24:53 | 0.23 | 0.77
2026-08-25T18:24:58 | 0.23 | 0.77
2026-08-25T18:25:03 | 0.45 | 0.77
2026-08-25T18:25:08 | 0.45 | 0.77
2026-08-25T18:25:13 | 0.45 | 0.77
2026-08-25T18:25:18 | 0.45 | 0.77
2026-08-25T18:25:23 | 0.45 | 0.77
2026-08-25T18:25:28 | 0.23 | 0.77
2026-08-25T18:25:33 | 0.45 | 0.77
2026-08-25T18:25:38 | 0.23 | 0.77
2026-08-25T18:25:44 | 0.23 | 0.77
2026-08-25T18:25:49 | 0.23 | 0.77
2026-08-25T18:25:54 | 0.23 | 0.77
2026-08-25T18:25:59 | 0.23 | 0.77
2026-08-25T18:26:04 | 0.23 | 0.77
2026-08-25T18:26:09 | 0.23 | 0.77
2026-08-25T18:26:14 | 0.23 | 0.77
2026-08-25T18:26:19 | 0.23 | 0.77
2026-08-25T18:26:24 | 0 | 0.77
2026-08-25T18:26:29 | 0.23 | 0.77
2026-08-25T18:26:35 | 0.23 | 0.77
2026-08-25T18:26:40 | 0 | 0.77
2026-08-25T18:26:45 | 0 | 0.77
2026-08-25T18:26:50 | 0 | 0.77
2026-08-25T18:26:55 | 0 | 0.77
2026-08-25T18:27:00 | 0 | 0.77
2026-08-25T18:27:06 | 0 | 0.77
2026-08-25T18:27:11 | 0.23 | 0.77
2026-08-25T18:27:17 | 0 | 0.77
2026-08-25T18:27:22 | 0 | 0.77
2026-08-25T18:27:27 | 0 | 0.77
2026-08-25T18:27:32 | 0 | 0.77
2026-08-25T18:27:37 | 0 | 0.77
2026-08-25T18:27:42 | 0 | 0.77
2026-08-25T18:27:47 | 0 | 0.77
2026-08-25T18:27:51 | 0 | 0.77
2026-08-25T18:27:56 | 0.23 | 0.77
2026-08-25T18:28:01 | 1.07 | 0.77
2026-08-25T18:28:06 | 0.31 | 0.77
2026-08-25T18:28:12 | 0.31 | 0.77
2026-08-25T18:28:17 | 0.31 | 0.77
2026-08-25T18:28:22 | 0.31 | 0.77
2026-08-25T18:28:27 | 0.31 | 0.77
2026-08-25T18:28:32 | 0.63 | 0.77
2026-08-25T18:28:37 | 0.63 | 0.77
2026-08-25T18:28:42 | 0.63 | 0.77
2026-08-25T18:28:47 | 0.93 | 0.77
2026-08-25T18:28:52 | 0.45 | 0.77
2026-08-25T18:28:57 | 0.45 | 0.77
2026-08-25T18:29:03 | 0.23 | 0.77
2026-08-25T18:29:08 | 0.23 | 0.77
2026-08-25T18:29:13 | 0 | 0.77
2026-08-25T18:29:18 | 0.23 | 0.77
2026-08-25T18:29:23 | 0.23 | 0.77
2026-08-25T18:29:28 | 0.45 | 0.77
2026-08-25T18:29:33 | 0.45 | 0.77
2026-08-25T18:29:38 | 0.45 | 0.77
2026-08-25T18:29:43 | 0.45 | 0.77
2026-08-25T18:29:48 | 0.45 | 0.77
2026-08-25T18:29:54 | 0.45 | 0.77
2026-08-25T18:29:59 | 0.45 | 0.77
2026-08-25T18:30:04 | 0.31 | 0.77
2026-08-25T18:30:09 | 0.31 | 0.77
2026-08-25T18:30:14 | 0.31 | 0.77
2026-08-25T18:30:19 | 0.31 | 0.77
2026-08-25T18:30:24 | 0.31 | 0.77
2026-08-25T18:30:30 | 0.45 | 0.77
2026-08-25T18:30:35 | 0.45 | 0.77
2026-08-25T18:30:40 | 0.37 | 0.77
2026-08-25T18:30:46 | 0.19 | 0.77
2026-08-25T18:30:51 | 0.19 | 0.77
2026-08-25T18:30:56 | 0.23 | 0.77
2026-08-25T18:31:01 | 0.23 | 0.77
2026-08-25T18:31:06 | 0.23 | 0.35
2026-08-25T18:31:11 | 0.23 | 0.35
2026-08-25T18:31:16 | 0.45 | 0.35
2026-08-25T18:31:21 | 0.23 | 0.35
2026-08-25T18:31:26 | 0.23 | 0
2026-08-25T18:31:31 | 0.45 | 0.35
2026-08-25T18:31:38 | 0.45 | 0.36
2026-08-25T18:31:43 | 0.45 | 0.36
2026-08-25T18:31:48 | 0.45 | 0.36
2026-08-25T18:31:53 | 0.45 | 0.36
2026-08-25T18:31:58 | 0.23 | 0
2026-08-25T18:32:03 | 0.23 | 0.35
2026-08-25T18:32:08 | 0.68 | 0
2026-08-25T18:32:13 | 0.45 | 0
2026-08-25T18:32:18 | 0.45 | 0.9
2026-08-25T18:32:23 | 0.23 | 0.9
2026-08-25T18:32:29 | 0.23 | 0
2026-08-25T18:32:34 | 0 | 0
2026-08-25T18:32:39 | 0 | 0
2026-08-25T18:32:44 | 0 | 0
2026-08-25T18:32:49 | 0.23 | 0
2026-08-25T18:32:54 | 0.45 | 0
2026-08-25T18:32:59 | 0.23 | 0
2026-08-25T18:33:04 | 0.45 | 0
2026-08-25T18:33:09 | 0.45 | 0
2026-08-25T18:33:14 | 0.23 | 0
2026-08-25T18:33:20 | 0.45 | 0
2026-08-25T18:33:25 | 0.45 | 0
2026-08-25T18:33:31 | 0 | 0
2026-08-25T18:33:36 | 0.45 | 0
2026-08-25T18:33:41 | 0.45 | 0
2026-08-25T18:33:46 | 0.45
2026-08-25T18:33:51
2026-08-25T18:33:56
2026-08-25T18:34:01
2026-08-25T18:34:06
2026-08-25T18:34:12
2026-08-25T18:34:17
2026-08-25T18:34:22
2026-08-25T18:34:27
2026-08-25T18:34:32
2026-08-25T18:34:37
2026-08-25T18:34:42
2026-08-25T18:34:47
2026-08-25T18:34:53
2026-08-25T18:34:59
2026-08-25T18:35:04
2026-08-25T18:35:09
2026-08-25T18:35:14
2026-08-25T18:35:19
2026-08-25T18:35:24
2026-08-25T18:35:29
2026-08-25T18:35:34
2026-08-25T18:35:39
2026-08-25T18:35:44
2026-08-25T18:35:49
2026-08-25T18:36:05
2026-08-25T18:36:10
2026-08-25T18:36:16
2026-08-25T18:36:21
2026-08-26T16:43:27 | 0.44 | 16.9
2026-08-26T16:43:32 | 2.4 | 14.22
2026-08-26T16:43:37 | 1.92 | 22.05
2026-08-26T16:43:42 | 2.12 | 14.72
2026-08-26T16:43:47 | 0.1 | 20.01
2026-08-26T16:43:52 | 0.41 | 9.96
2026-08-26T16:43:57 | 2.37 | 17.37
2026-08-26T16:44:02 | 1.03 | 18.78
2026-08-26T16:44:07 | 1.94 | 17.05
2026-08-26T16:44:12 | 2.71 | 19.5
2026-08-26T16:44:17 | 2.6 | 16.74
2026-08-26T16:44:22 | 1.6 | 16.94
2026-08-26T16:44:27 | 1.89 | 12.35
2026-08-26T16:44:32 | 1.79 | 22.29
2026-08-26T16:44:37 | 1.12 | 21.99
2026-08-26T16:44:42 | 2.25 | 13.79
2026-08-26T16:44:47 | 2.05 | 20.58
2026-08-26T16:44:52 | 0.99 | 14.64
2026-08-26T16:44:57 | 2.99 | 10.57
2026-08-26T16:45:02 | 1.94 | 23.03
2026-08-26T16:45:07 | 1.44 | 11.53
2026-08-26T16:45:12 | 2.12 | 18.7
2026-08-26T16:45:17 | 1.78 | 14.04
2026-08-26T16:45:22 | 2.03 | 15.75
2026-08-26T16:45:27 | 0.55 | 17.45
2026-08-26T16:45:32 | 2.55 | 21.48
2026-08-26T16:45:37 | 2.33 | 19.72
2026-08-26T16:45:53 | 2.67 | 92.31
2026-08-26T16:45:58 | 1.16 | 94.78
2026-08-26T16:46:03 | 0.26 | 93.04
2026-08-26T16:46:08 | 1.22 | 86.98
2026-08-26T16:46:13 | 1.66 | 90.63
2026-08-26T16:46:18 | 0.8 | 102.23
2026-08-26T16:46:23 | 0.9 | 96.36
2026-08-26T16:46:28 | 2.84 | 89.82
2026-08-26T16:46:33 | 1.26 | 101.35
2026-08-26T16:46:38 | 1.12 | 108.65
2026-08-26T16:46:43 | 0.48 | 77.59
2026-08-26T16:46:48 | 1.04 | 92.42
2026-08-26T16:46:53 | 2.52 | 71.94
2026-08-26T16:46:58 | 0.91 | 110.41
2026-08-26T16:47:03 | 1.2 | 103.74
2026-08-26T16:47:08 | 2.78 | 101.51
2026-08-26T16:47:13 | 2.39 | 84.41
2026-08-26T16:47:18 | 0.15 | 98.7
2026-08-26T16:47:23 | 2.41 | 78.55
2026-08-26T16:47:29 | 0.97 | 57.69
2026-08-26T16:47:34 | 1.27 | 99.68
2026-08-26T16:47:39 | 2.31 | 108.63
2026-08-26T16:47:44 | 0.51 | 75.73
2026-08-26T16:47:49 | 2.94 | 81.81
2026-08-26T16:47:54 | 3.26 | 108.03
2026-08-26T16:47:59 | 2.37 | 90.49
2026-08-26T16:48:04 | 1.02 | 71.79
2026-08-26T16:48:09 | 2.43 | 81.47
2026-08-26T16:48:14 | 2.13 | 84.46
2026-08-26T16:48:19 | 1.57 | 94.12
2026-08-26T16:48:24 | 0.29 | 99.02
2026-08-26T16:48:29 | 1.76 | 83.73
2026-08-26T16:48:34 | 2.14 | 110.54
2026-08-26T16:48:39 | 1.64 | 70.63
2026-08-26T16:48:44 | 0.63 | 91.72
2026-08-26T16:48:49 | 1.29 | 78.87
2026-08-26T16:48:54 | 1.93 | 93.08
2026-08-26T16:48:59 | 1.78 | 73.84
2026-08-26T16:49:04 | 2 | 109.97
2026-08-26T16:49:09 | 2.09 | 90.88
2026-08-26T16:49:14 | 0.74 | 87.82
2026-08-26T16:49:19 | 3.14 | 68.4
2026-08-26T16:49:24 | 0.99 | 111.14
2026-08-26T16:49:29 | 2.1 | 84.95
2026-08-26T16:49:34 | 0.96 | 94.5
2026-08-26T16:49:39 | 1.53 | 87.9
2026-08-26T16:49:44 | 2.64 | 107.24
2026-08-26T16:49:49 | 2.07 | 82.32
2026-08-26T16:49:54 | 1.7 | 79.38
2026-08-26T16:49:59 | 3.2 | 112.8
2026-08-26T16:50:04 | 1.59 | 93.25
2026-08-26T16:50:09 | 0.98 | 106.32
2026-08-26T16:50:14 | 1.58 | 92.22
2026-08-26T16:50:19 | 0.97 | 93.11
2026-08-26T16:50:24 | 2.17 | 64.6
2026-08-26T16:50:29 | 1.33 | 76.81
2026-08-26T16:50:34 | 0.48 | 104.96
2026-08-26T16:50:39 | 1 | 67.88
2026-08-26T16:50:44 | 1.2 | 85.77
2026-08-26T16:50:49 | 0.82 | 83.65
2026-08-26T16:50:54 | 2.8 | 108.28
2026-08-26T16:50:59 | 1.49 | 113.72
2026-08-26T16:51:04 | 2.06 | 90.05
2026-08-26T16:51:09 | 1.54 | 72.88
2026-08-26T16:51:14 | 2.45 | 77.31
2026-08-26T16:51:19 | 1.34 | 103.45
2026-08-26T16:51:24 | 1.64 | 93.69
2026-08-26T16:51:29 | 0.99 | 86.62
2026-08-26T17:02:31 |  | 413.79
2026-08-26T17:02:37 | 2.6 | 339.94
2026-08-26T17:02:42 | 2.78 | 299.25
2026-08-26T17:02:48 | 2.8 | 300.38
2026-08-26T17:02:53 | 2.81 | 300.38
2026-08-26T17:02:58 | 2.61 | 300.75
2026-08-26T17:03:03 | 2.61 | 300.75
2026-08-26T17:03:08 | 2.61 | 300.75
2026-08-26T17:03:14 | 2.39 | 300.75
2026-08-26T17:03:19 | 2.81 | 300.38
2026-08-26T17:03:24 | 2.8 | 300.38
2026-08-26T17:03:29 | 2.56 | 299.25
2026-08-26T17:03:34 | 2.57 | 299.25
2026-08-26T17:03:40 | 2.37 | 299.63
2026-08-26T17:03:45 | 2.38 | 300.38
2026-08-26T17:03:50 | 2.38 | 300.38
2026-08-26T17:03:55 | 2.38 | 300.38
2026-08-26T17:04:00 | 2.6 | 300.38
2026-08-26T17:04:05 | 2.6 | 300.38
2026-08-26T17:04:11 | 2.6 | 300.38
2026-08-26T17:04:16 | 2.6 | 300.38
2026-08-26T17:04:22 | 2.6 | 300.38
2026-08-26T17:04:27 | 2.82 | 300.38
2026-08-26T17:04:32 | 2.82 | 300.38
2026-08-26T17:04:38 | 2.6 | 300.38
2026-08-26T17:04:44 | 2.6 | 300.38
2026-08-26T17:04:49 | 2.6 | 300.38
2026-08-26T17:04:54 | 2.6 | 300.38
2026-08-26T17:04:59 | 2.83 | 300.75
2026-08-26T17:05:04 | 2.84 | 300.75
2026-08-26T17:05:09 | 2.84 | 300.75
2026-08-26T17:05:15 | 2.84 | 300.75
2026-08-26T17:05:20 | 2.62 | 301.13
2026-08-26T17:05:25 | 2.85 | 301.51
2026-08-26T17:05:30 | 2.81 | 300.38
2026-08-26T17:05:35 | 2.82 | 300.38
2026-08-26T17:05:41 | 2.82 | 300.38
2026-08-26T17:05:46 | 2.77 | 299.25
2026-08-26T17:05:51 | 2.79 | 299.25
2026-08-26T17:05:56 | 2.79 | 299.63
2026-08-26T17:06:01 | 2.57 | 299.25
2026-08-26T17:06:06 | 2.79 | 299.25
2026-08-26T17:06:12 | 2.79 | 299.25
2026-08-26T17:06:17 | 3.01 | 299.63
2026-08-26T17:06:22 | 2.61 | 300.38
2026-08-26T17:06:27 | 2.61 | 300.38
2026-08-26T17:06:32 | 2.39 | 300.38
2026-08-26T17:06:38 | 2.61 | 300.38
2026-08-26T17:06:43 | 2.61 | 300.38
2026-08-26T17:06:48 | 2.82 | 300.38
2026-08-26T17:06:53 | 2.82 | 300.38
2026-08-26T17:06:58 | 2.82 | 300.38
2026-08-26T17:07:04 | 2.82 | 300.38
2026-08-26T17:07:09 | 2.82 | 300.38
2026-08-26T17:07:14 | 2.82 | 300.38
2026-08-26T17:07:19 | 2.6 | 300.38
2026-08-26T17:07:24 | 2.81 | 300.38
2026-08-26T17:07:29 | 2.6 | 300.38
2026-08-26T17:07:35 | 2.59 | 300.38
2026-08-26T17:07:41 | 2.57 | 299.25
2026-08-26T17:07:46 | 2.58 | 299.63
2026-08-26T17:07:53 | 2.8 | 299.63
2026-08-26T17:07:58 | 2.79 | 299.63
2026-08-26T17:08:03 | 2.58 | 299.63
2026-08-26T17:08:09 | 2.57 | 299.25
2026-08-26T17:08:14 | 2.78 | 299.25
2026-08-26T17:08:19 | 2.78 | 299.25
2026-08-26T17:08:25 | 2.78 | 299.25
2026-08-26T17:08:30 | 2.78 | 299.25
2026-08-26T17:08:35 | 2.56 | 299.25
2026-08-26T17:08:40 | 2.99 | 299.25
2026-08-26T17:08:47 | 2.99 | 299.25
2026-08-26T17:08:52 | 2.78 | 299.25
2026-08-26T17:08:58 | 2.78 | 299.25
2026-08-26T17:09:03 | 2.78 | 299.25
2026-08-26T17:09:08 | 2.78 | 299.25
2026-08-26T17:09:14 | 2.78 | 299.25
2026-08-26T17:09:19 | 2.62 | 300.75
2026-08-26T17:09:24 | 2.4 | 300.75
2026-08-26T17:09:29 | 2.79 | 299.63
2026-08-26T17:09:34 | 2.97 | 298.51
2026-08-26T17:09:39 | 2.75 | 298.14
2026-08-26T17:09:45 | 2.75 | 298.14
2026-08-26T17:09:50 | 2.75 | 281.36
2026-08-26T17:09:55 | 2.77 | 281.69
2026-08-26T17:10:00 | 2.55 | 281.36
2026-08-26T17:10:05 | 2.54 | 281.36
2026-08-26T17:10:11 | 2.75 | 281.36
2026-08-26T17:10:16 | 2.75 | 281.36
2026-08-26T17:10:21 | 2.97 | 281.36
2026-08-26T17:10:29 | 2.75 | 281.36
2026-08-26T17:10:34 | 2.98 | 281.69
2026-08-26T17:10:40 | 2.97 | 281.36
2026-08-26T17:10:45 | 2.75 | 281.36
2026-08-26T17:10:51 | 2.77 | 281.69
2026-08-26T17:10:56 | 2.77 | 281.69
2026-08-26T17:11:01 | 2.99 | 281.69
2026-08-26T17:11:06 | 2.77 | 281.69
2026-08-26T17:11:11 | 2.75 | 281.36
2026-08-26T17:11:17 | 2.75 | 281.36
2026-08-26T17:11:22 | 2.76 | 281.36
2026-08-26T17:11:27 | 2.76 | 281.36
2026-08-26T17:11:32 | 2.76 | 281.69
2026-08-26T17:11:37 | 2.55 | 281.69
2026-08-26T17:11:42 | 2.55 | 281.69
2026-08-26T17:11:49 | 2.75 | 281.36
2026-08-26T17:11:55 | 2.76 | 281.36
2026-08-26T17:12:00 | 2.76 | 281.36
2026-08-26T17:12:05 | 2.56 | 281.69
2026-08-26T17:12:10 | 2.56 | 282.35
2026-08-26T17:12:16 | 2.34 | 281.69
2026-08-26T17:12:21 | 2.55 | 281.69
2026-08-26T17:12:26 | 2.55 | 281.69
2026-08-26T17:12:31 | 2.55 | 281.69
2026-08-26T17:12:37 | 2.55 | 281.69
2026-08-26T17:12:44 | 2.55 | 281.69
2026-08-26T17:12:49 | 2.55 | 281.36
2026-08-26T17:12:54 | 2.55 | 281.36
2026-08-26T17:13:00 | 2.13 | 200
2026-08-26T17:13:09 | 2.75 | 281.36
2026-08-26T17:13:15 | 2.75 | 281.36
2026-08-26T17:13:20 | 2.54 | 281.36
2026-08-26T17:13:25 | 2.95 | 287.43
2026-08-26T17:13:31 | 2.72 | 287.43
2026-08-26T17:13:36 | 2.94 | 287.43
2026-08-26T17:13:42 | 2.72 | 287.43
2026-08-26T17:13:47 | 2.72 | 287.43
2026-08-26T17:13:52 | 2.72 | 287.43
2026-08-26T17:13:57 | 2.72 | 287.43
2026-08-26T17:14:02 | 2.49 | 287.43
2026-08-26T17:14:08 | 2.72 | 287.43
2026-08-26T17:14:13 | 2.47 | 286.74
2026-08-26T17:14:20 | 2.58 | 282.69
2026-08-26T17:14:25 | 2.6 | 283.35
2026-08-26T17:14:30 | 2.81 | 283.35
2026-08-26T17:14:35 | 2.59 | 283.35
2026-08-26T17:14:41 | 2.59 | 283.35
2026-08-26T17:14:46 | 2.37 | 283.35
2026-08-26T17:14:51 | 2.59 | 282.69
2026-08-26T17:15:07 | 2.59 | 283.35
2026-08-26T17:15:13 | 2.81 | 283.35
2026-08-26T17:15:18 | 2.8 | 283.02
2026-08-26T17:15:23 | 2.38 | 283.35
2026-08-26T17:15:28 | 2.6 | 283.35
2026-08-26T17:15:34 | 2.6 | 283.35
2026-08-26T17:15:41 | 2.81 | 283.35
2026-08-26T17:15:46 | 2.8 | 283.02
2026-08-26T17:15:51 | 2.6 | 283.35
2026-08-26T17:15:56 | 2.8 | 282.69
2026-08-26T17:16:01 | 2.6 | 283.35
2026-08-26T17:16:08 | 2.6 | 283.35
2026-08-26T17:16:13 | 2.81 | 283.35
2026-08-26T17:16:18 | 2.8 | 283.35
2026-08-26T17:16:23 | 2.59 | 283.35
2026-08-26T17:16:28 | 2.59 | 283.35
2026-08-26T17:16:34 | 2.81 | 283.35
2026-08-26T17:16:39 | 2.81 | 283.35
2026-08-26T17:16:44 | 2.6 | 283.35
2026-08-26T17:16:49 | 2.38 | 283.35
2026-08-26T17:16:54 | 2.6 | 284.02
2026-08-26T17:17:00 | 2.6 | 284.02
2026-08-26T17:17:05 | 2.6 | 283.69
2026-08-26T17:17:10 | 2.6 | 283.69
2026-08-26T17:17:15 | 2.82 | 284.02
2026-08-26T17:17:20 | 2.81 | 284.02
2026-08-26T17:17:26 | 2.81 | 284.02
2026-08-26T17:17:31 | 2.81 | 283.69
2026-08-26T17:17:36 | 3.03 | 283.69
2026-08-26T17:17:41 | 3.03 | 283.69
2026-08-26T17:17:46 | 3.03 | 283.69
2026-08-26T17:17:51 | 2.82 | 284.02
2026-08-26T17:17:57 | 3.03 | 283.69
2026-08-26T17:18:02 | 2.6 | 283.69
2026-08-26T17:18:07 | 2.6 | 283.69
2026-08-26T17:18:12 | 2.38 | 284.02
2026-08-26T17:18:17 | 2.6 | 283.69
2026-08-26T17:18:23 | 2.6 | 283.69
2026-08-26T17:18:28 | 2.81 | 283.69
2026-08-26T17:18:33 | 2.8 | 283.69
2026-08-26T17:18:38 | 2.59 | 283.69
2026-08-26T17:18:43 | 2.6 | 283.69
2026-08-26T17:18:49 | 2.6 | 283.69
2026-08-26T17:18:54 | 2.82 | 283.69
2026-08-26T17:18:59 | 2.6 | 283.69
2026-08-26T17:19:04 | 2.6 | 283.69
2026-08-26T17:19:09 | 2.38 | 283.69
2026-08-26T17:19:15 | 2.38 | 283.69
2026-08-26T17:19:20 | 2.38 | 283.69
2026-08-26T17:19:25 | 2.38 | 283.69
2026-08-26T17:19:30 | 2.6 | 284.02
2026-08-26T17:19:35 | 2.6 | 284.36
2026-08-26T17:19:41 | 2.6 | 284.36
2026-08-26T17:21:57 | 1.13 | 413.79
2026-08-26T17:22:02 | 0.44 | 283.69
2026-08-26T17:22:07 | 0.44 | 283.69
2026-08-26T17:22:12 | 0.44 | 283.35
2026-08-26T17:22:18 | 0.22 | 282.69
2026-08-26T17:22:23 | 0.43 | 283.35
2026-08-26T17:22:28 | 0.22 | 282.69
2026-08-26T17:22:33 | 0.44 | 285.37
2026-08-26T17:22:38 | 0.22 | 285.04
2026-08-26T17:22:43 | 0.22 | 283.35
2026-08-26T17:22:49 | 0.43 | 283.35
2026-08-26T17:22:54 | 0.22 | 282.69
2026-08-26T17:22:59 | 0.43 | 283.35
2026-08-26T17:23:04 | 0.44 | 283.35
2026-08-26T17:23:11 | 0.44 | 283.69
2026-08-26T17:23:17 | 0.65 | 283.35
2026-08-26T17:23:22 | 0.44 | 283.69
2026-08-26T17:23:27 | 0.66 | 283.69
2026-08-26T17:23:32 | 0.44 | 283.69
2026-08-26T17:23:39 | 0.44 | 283.69
2026-08-26T17:23:44 | 0.44 | 283.69
2026-08-26T17:23:50 | 0.44 | 283.69
2026-08-26T17:23:55 | 0.44 | 283.69
2026-08-26T17:24:00 | 0.44 | 284.02
2026-08-26T17:24:06 | 0.44 | 284.36
2026-08-26T17:24:11 | 0.44 | 284.36
2026-08-26T17:24:16 | 0.66 | 283.69
2026-08-26T17:24:22 | 0.66 | 284.02
2026-08-26T17:24:27 | 0.66 | 284.02
2026-08-26T17:24:33 | 0.66 | 283.69
2026-08-26T17:24:38 | 0.66 | 283.69
2026-08-26T17:24:43 | 0.66 | 283.69
2026-08-26T17:24:48 | 0.66 | 283.69
2026-08-26T17:24:53 | 0.66 | 284.36
2026-08-26T17:24:59 | 0.44 | 284.36
2026-08-26T17:25:04 | 0.44 | 284.36
2026-08-26T17:25:09 | 0.44 | 284.36
2026-08-26T17:25:14 | 0.44 | 284.36
2026-08-26T17:25:19 | 0.44 | 284.36
2026-08-26T17:25:25 | 0.44 | 284.36
2026-08-26T17:25:31 | 0.44 | 284.36
2026-08-26T17:25:37 | 0.44 | 284.02
2026-08-26T17:25:42 | 0.44 | 284.02
2026-08-26T17:25:47 | 0.44 | 284.02
2026-08-26T17:25:53 | 0.44 | 284.02
2026-08-26T17:25:58 | 0.44 | 284.36
2026-08-26T17:26:03 | 0.44 | 284.36
2026-08-26T17:26:08 | 0.44 | 284.36
2026-08-26T17:26:13 | 0.44 | 284.36
2026-08-26T17:26:21 | 0.44 | 284.02
2026-08-26T17:26:27 | 0.44 | 284.02
2026-08-26T17:26:33 | 0.44 | 283.69
2026-08-26T17:26:38 | 0.44 | 283.69
2026-08-26T17:26:43 | 0.22 | 283.69
2026-08-26T17:26:50 | 0.22 | 182.46
2026-08-26T17:26:56 | 0.22 | 182.46
2026-08-26T17:27:01 | 0.22 | 182.46
2026-08-26T17:27:06 | 0.22 | 182.46
2026-08-26T17:27:11 | 0.44 | 182.46
2026-08-26T17:27:16 | 0.66 | 182.46
2026-08-26T17:27:21 | 0.22 | 182.46
2026-08-26T17:27:27 | 0.44 | 182.46
2026-08-26T17:27:33 | 0.44 | 181.69
2026-08-26T17:27:38 | 0.22 | 181.69
2026-08-26T17:27:43 | 0.22 | 181.69
2026-08-26T17:27:48 | 0.22 | 181.69
2026-08-26T17:27:54 | 0.44 | 181.69
2026-08-26T17:28:00 | 0.44 | 181.69
2026-08-26T17:28:05 | 0.22 | 181.69
2026-08-26T17:28:10 | 0.22 | 181.69
2026-08-26T17:28:16 | 0.22 | 181.69
2026-08-26T17:28:22 | 0.22 | 181.69
2026-08-26T17:28:27 | 0.44 | 181.69
2026-08-26T17:28:32 | 0.44 | 181.69
2026-08-26T17:28:37 | 0.65 | 181.69
2026-08-26T17:28:43 | 0.44 | 181.69
2026-08-26T17:28:48 | 0.44 | 181.69
2026-08-26T17:28:53 | 0.44 | 181.69
2026-08-26T17:28:58 | 0.65 | 181.69
2026-08-26T17:29:04 | 0.44 | 181.69
2026-08-26T17:33:45 | 0.44 | 298.47
2026-08-26T17:33:50 | 0.66 | 298.47
2026-08-26T17:33:55 | 0.44 | 298.47
2026-08-26T17:34:01 | 0.44 | 298.47
2026-08-26T17:34:06 | 0.44 | 298.47
2026-08-26T17:34:11 | 0.44 | 298.47
2026-08-26T17:34:16 | 0.22 | 298.47
2026-08-26T17:34:21 | 0.44 | 298.47
2026-08-26T17:34:27 | 0.44 | 298.47
2026-08-26T17:34:32 | 0.44 | 298.47
2026-08-26T17:34:39 | 0.44 | 182.81
2026-08-26T17:34:44 | 0.22 | 182.81
2026-08-26T17:34:49 | 0.44 | 182.81
2026-08-26T17:34:55 | 0.66 | 182.81
2026-08-26T17:35:03 | 0.66 | 298.47
2026-08-26T17:35:08 | 0.44 | 298.47
2026-08-26T17:35:13 | 0.44 | 298.47
2026-08-26T17:35:19 | 0.44 | 298.47
2026-08-26T17:35:24 | 0.66 | 298.47
2026-08-26T17:35:29 | 0.89 | 298.47
2026-08-26T17:35:37 | 0.67 | 298.59
2026-08-26T17:35:43 | 0.44 | 298.59
2026-08-26T17:35:48 | 0.44 | 298.47
2026-08-26T17:35:53 | 0.44 | 298.47
2026-08-26T17:35:59 | 0.22 | 298.47
2026-08-26T17:36:04 | 0.22 | 298.47
2026-08-26T17:36:10 | 0.22 | 298.47
2026-08-26T17:36:15 | 0.22 | 298.47
2026-08-26T17:36:20 | 0.22 | 298.59
2026-08-26T17:36:25 | 0.44 | 298.59
2026-08-26T17:36:30 | 0.44 | 298.47
2026-08-26T17:36:36 | 0.44 | 298.47
2026-08-26T17:36:41 | 0.44 | 298.59
2026-08-26T17:36:46 | 0.44 | 298.59
2026-08-26T17:36:51 | 0.22 | 298.59
2026-08-26T17:36:56 | 0.44 | 298.59
2026-08-26T17:37:01 | 0.22 | 298.59
2026-08-26T17:37:07 | 0.22 | 298.59
2026-08-26T17:45:44 | 0.44 | 535.45
2026-08-26T17:45:50 | 0.44 | 535.45
2026-08-26T17:45:55 | 0.44 | 535.45
2026-08-26T17:46:00 | 0.44 | 535.45
2026-08-26T17:46:06 | 0.44 | 535.33
2026-08-26T17:46:11 | 0.44 | 535.22
2026-08-26T17:46:15 | 0.66 | 375.79
2026-08-26T17:46:20 | 0.44 | 375.79
2026-08-26T17:46:25 | 0.44 | 375.79
2026-08-26T17:46:30 | 0.44 | 535.22
2026-08-26T17:46:35 | 0.44 | 535.22
2026-08-26T17:46:41 | 0.44 | 535.22
2026-08-26T17:46:47 | 0.22 | 535.22
2026-08-26T17:46:52 | 0.22 | 507.39
2026-08-26T17:46:58 | 0.44 | 507.61
2026-08-26T17:47:07 | 0.44 | 375.91
2026-08-26T17:47:12 | 0.44 | 375.91
2026-08-26T17:47:17 | 0.44 | 375.91
2026-08-26T17:47:22 | 0.22 | 375.91
2026-08-26T17:47:28 | 0.44 | 375.91
2026-08-26T17:47:33 | 0.22 | 375.91
2026-08-26T17:47:38 | 0.22 | 375.91
2026-08-26T17:47:43 | 0.44 | 375.91
2026-08-26T17:47:48 | 0.22 | 375.91
2026-08-26T17:47:53 | 0.44 | 375.91
2026-08-26T17:47:59 | 0.44 | 375.91
2026-08-26T17:48:04 | 0.44 | 375.91
2026-08-26T17:48:09 | 0.44 | 375.91
2026-08-26T17:48:14 | 0.44 | 375.91
2026-08-26T17:48:19 | 0.44 | 375.85
2026-08-26T17:48:26 | 0.44 | 375.85
2026-08-26T17:48:31 | 0.44 | 375.79
2026-08-26T17:48:36 | 0.44 | 375.85
2026-08-26T17:48:41 | 0.44 | 375.79
2026-08-26T17:48:48 | 0.44 | 375.79
2026-08-26T17:48:53 | 0.44 | 375.79
2026-08-26T17:48:58 | 0.44 | 375.79
2026-08-26T17:49:04 | 0.44 | 375.79
2026-08-26T17:49:09 | 0.66 | 375.79
2026-08-26T17:49:14 | 0.44 | 375.79
2026-08-26T17:52:00 | 0.66 | 182.46
2026-08-26T17:52:06 | 0.88 | 182.46
2026-08-26T17:52:11 | 0.66 | 182.46
2026-08-26T17:52:16 | 0.66 | 182.46
2026-08-26T17:52:22 | 0.66 | 182.46
2026-08-26T17:52:27 | 0.66 | 182.46
2026-08-26T17:52:32 | 0.66 | 182.46
2026-08-26T17:52:37 | 0.66 | 182.46
2026-08-26T17:52:42 | 0.44 | 182.46
2026-08-26T17:52:48 | 0.44 | 182.46
2026-08-26T17:52:53 | 0.66 | 182.46
2026-08-26T17:52:58 | 0.44 | 182.46
2026-08-26T17:53:03 | 0.44 | 182.46
2026-08-26T17:53:08 | 0.44 | 182.46
2026-08-26T17:53:13 | 0.44 | 182.46
2026-08-26T17:53:19 | 0.44 | 182.46
2026-08-26T17:53:24 | 0.66 | 181.69
2026-08-26T17:53:29 | 0.66 | 181.69
2026-08-26T17:53:34 | 0.66 | 181.69
2026-08-26T17:53:39 | 0.66 | 181.69
2026-08-26T17:53:45 | 0.44 | 181.69
2026-08-26T17:53:50 | 0.44 | 182.46
2026-08-26T17:53:55 | 0.44 | 182.46
2026-08-26T17:54:00 | 0.44 | 181.69
2026-08-26T17:54:05 | 0.44 | 181.69
2026-08-26T17:54:10 | 0.44 | 181.69
2026-08-26T17:54:16 | 0.44 | 181.69
2026-08-27T12:19:59
2026-08-27T12:20:09
2026-08-27T12:20:16
2026-08-27T12:20:24
2026-08-27T12:20:31 | 1.4
2026-08-27T12:20:40 | 0
2026-08-27T12:20:48 | 0
2026-08-27T12:20:55 | 0
2026-08-27T12:21:05 | 0
2026-08-27T12:21:14 | 0
2026-08-27T12:21:40 | 0.46 | 194.37
2026-08-27T12:21:45 | 0.46 | 194.37
2026-08-27T12:21:50 | 0.23 | 194.37
2026-08-27T12:21:55 | 0.23 | 194.37
2026-08-27T12:22:00 | 0.46 | 194.37
2026-08-27T12:22:05 | 0.46 | 194.37
2026-08-27T12:22:11 | 0.46 | 194.37
2026-08-27T12:22:16 | 0.46 | 194.37
2026-08-27T12:22:21 | 0.46 | 194.37
2026-08-27T12:22:26 | 0.46 | 194.37
2026-08-27T12:22:31 | 0.46 | 194.37
2026-08-27T12:22:37 | 0.68 | 194.37
2026-08-27T12:22:42 | 0.45 | 194.17
2026-08-27T12:22:47 | 0.46 | 194.37
2026-08-27T12:22:53 | 0.46 | 194.37
2026-08-27T12:23:04
2026-08-27T12:23:44 | 0.46 | 278.05
2026-08-27T12:23:50 | 0.69 | 278.05
2026-08-27T12:23:55 | 0.68 | 278.05
2026-08-27T12:24:00 | 0.46 | 278.05
2026-08-27T12:24:06 | 0.46 | 278.05
2026-08-27T12:24:12 | 0.46 | 278.05
2026-08-27T12:24:18 | 0.68 | 278.05
2026-08-27T12:24:23 | 0.46 | 194.37
2026-08-27T12:24:28 | 0.46 | 194.37
2026-08-27T12:24:33 | 0.46 | 194.37
2026-08-27T12:24:38 | 0.46 | 194.37
2026-08-27T12:24:44 | 0.46 | 194.37
2026-08-27T12:24:49 | 0.46 | 194.37
2026-08-27T12:24:54 | 0.46 | 194.37
2026-08-27T12:24:59 | 0.46 | 194.37
2026-08-27T12:25:04 | 0.46 | 194.37
2026-08-27T12:25:11 | 0.46 | 194.37
2026-08-27T12:25:16 | 0.46 | 194.37
2026-08-27T12:25:21 | 0.46 | 194.37
2026-08-27T12:25:27 | 0.46 | 194.37
2026-08-27T12:25:33 | 0.46 | 194.37
2026-08-27T12:25:39 | 0.46 | 194.37
2026-08-27T12:25:45 | 0.46 | 194.37
2026-08-27T12:25:50 | 0.46 | 194.37
2026-08-27T12:25:55 | 0.46 | 194.37
2026-08-27T12:26:00 | 0.46 | 194.37
2026-08-27T12:26:06 | 0.46 | 194.37
2026-08-27T12:26:12 | 0.23 | 194.37
2026-08-27T12:26:17 | 0.23 | 194.37
2026-08-27T12:26:23 | 0.45 | 194.37
2026-08-27T12:26:28 | 0.68 | 194.37
2026-08-27T12:26:33 | 0.68 | 194.37
2026-08-27T12:26:39 | 0.68 | 194.37
2026-08-27T12:26:44 | 0.68 | 194.37
2026-08-27T12:26:49 | 0.69 | 194.37
2026-08-27T12:26:54 | 0.68 | 194.37
2026-08-27T12:26:59 | 0.68 | 194.37
2026-08-27T12:27:04 | 0.68 | 194.37
2026-08-27T12:27:10 | 0.91 | 194.37
2026-08-27T12:27:15 | 0.91 | 194.37
2026-08-27T12:27:20 | 0.68 | 194.37
2026-08-27T12:27:25 | 0.68 | 194.37
2026-08-27T12:27:30 | 0.68 | 194.37
2026-08-27T12:27:36 | 0.45 | 194.37
2026-08-27T12:27:41 | 0.68 | 194.37
2026-08-27T12:27:46 | 0.68 | 194.37
2026-08-27T12:27:51 | 0.68 | 194.37
2026-08-27T12:27:56 | 0.68 | 194.37
2026-08-27T12:28:01 | 0.68 | 194.37
2026-08-27T12:28:07 | 0.91 | 194.37
2026-08-27T12:28:12 | 0.45 | 194.37
2026-08-27T12:28:17 | 0.91 | 194.37
2026-08-27T12:28:22 | 0.91 | 194.37
2026-08-27T12:28:27 | 0.68 | 194.37
2026-08-27T12:28:33 | 0.68 | 194.37
2026-08-27T12:28:38 | 0.68 | 194.37
2026-08-27T12:28:43 | 0.45 | 194.37
2026-08-27T12:28:48 | 0.68 | 194.37
2026-08-27T12:28:53 | 0.68 | 194.37
2026-08-27T12:28:58 | 0.68 | 194.37
2026-08-27T12:29:04 | 0.91 | 194.37
2026-08-27T12:29:09 | 0.68 | 194.37
2026-08-27T12:29:15 | 0.45 | 194.37
2026-08-27T12:29:20 | 0.45 | 194.37
2026-08-27T12:29:25 | 0.45 | 194.37
2026-08-27T12:29:30 | 0.68 | 194.37
2026-08-27T12:29:36 | 0.45 | 194.37
2026-08-27T12:29:42 | 0.45 | 194.37
2026-08-27T12:29:47 | 0.68 | 194.37
2026-08-27T12:29:52 | 0.68 | 194.37
2026-08-27T12:29:58 | 0.68 | 194.37
2026-08-27T12:30:03 | 0.68 | 194.37
2026-08-27T12:30:08 | 0.68 | 194.37
2026-08-27T12:30:13 | 0.68 | 194.37
2026-08-27T12:30:18 | 0.45 | 194.37
2026-08-27T12:30:23 | 0.68 | 194.37
2026-08-27T12:30:29 | 0.68 | 194.37
2026-08-27T12:30:34 | 0.45 | 194.37
2026-08-27T12:30:39 | 0.45 | 194.37
2026-08-27T12:30:44 | 0.45 | 194.37
2026-08-27T12:30:49 | 0.68 | 194.37
2026-08-27T12:30:54 | 0.45 | 194.37
2026-08-27T12:31:00 | 0.45 | 194.37
2026-08-27T12:31:05 | 0.68 | 194.37
2026-08-27T12:31:10 | 0.68 | 194.37
2026-08-27T12:31:15 | 0.68 | 194.37
2026-08-27T12:31:20 | 0.45 | 194.37
2026-08-27T12:31:26 | 0.68 | 194.37
2026-08-27T12:31:32 | 0.68 | 194.37
2026-08-27T12:31:37 | 0.68 | 194.37
2026-08-27T12:31:42 | 0.68 | 194.37
2026-08-27T12:31:47 | 0.45 | 194.37
2026-08-27T12:31:52 | 0.45 | 194.37
2026-08-27T12:31:58 | 0.45 | 194.37
2026-08-27T12:32:03 | 0.45 | 194.37
2026-08-27T12:32:08 | 0.68 | 194.37
2026-08-27T12:32:13 | 0.68 | 194.37
2026-08-27T12:32:18 | 0.68 | 194.37
2026-08-27T12:32:23 | 0.68 | 194.37
2026-08-27T12:32:29 | 0.45 | 194.37
2026-08-27T12:32:34 | 0.68 | 194.37
2026-08-27T12:32:39 | 0.68 | 194.37
2026-08-27T12:32:44 | 0.46 | 194.37
2026-08-27T12:32:49 | 0.46 | 194.37
2026-08-27T12:32:55 | 0.46 | 194.37
2026-08-27T12:33:00 | 0.46 | 194.37
2026-08-27T12:33:05 | 0.68 | 194.37
2026-08-27T12:33:10 | 0.68 | 194.37
2026-08-27T12:33:15 | 0.68 | 194.37
2026-08-27T12:33:21 | 0.68 | 194.37
2026-08-27T12:33:28 | 0.68 | 194.37
2026-08-27T12:33:34 | 0.68 | 194.37
2026-08-27T12:33:39 | 0.68 | 194.37
2026-08-27T12:33:44 | 0.68 | 194.37
2026-08-27T12:33:51 | 0.45 | 194.37
2026-08-27T12:33:56 | 0.91 | 194.37
2026-08-27T12:34:01 | 0.91 | 194.37
2026-08-27T12:34:06 | 0.68 | 194.37
2026-08-27T12:34:11 | 0.91 | 194.37
2026-08-27T12:34:16 | 0.68 | 194.37
2026-08-27T12:34:23 | 0.91 | 194.37
2026-08-27T12:34:28 | 0.45 | 194.37
2026-08-27T12:34:33 | 0.68 | 194.37
2026-08-27T12:34:38 | 0.68 | 194.37
2026-08-27T12:34:43 | 0.45 | 194.37
2026-08-27T12:34:48 | 0.45 | 194.37
2026-08-27T12:34:54 | 0.45 | 194.37
2026-08-27T12:34:59 | 0.45 | 194.37
2026-08-27T12:35:04 | 0.68 | 194.37
2026-08-27T12:35:09 | 0.68 | 194.37
2026-08-27T12:35:14 | 0.68 | 194.37
2026-08-27T12:35:20 | 0.68 | 194.37
2026-08-27T12:35:25 | 0.46 | 194.37
2026-08-27T12:35:30 | 0.45 | 194.37
2026-08-27T12:35:35 | 0.45 | 194.37
2026-08-27T12:35:40 | 0.45 | 194.37
2026-08-27T12:35:45 | 0.45 | 194.37
2026-08-27T12:35:51 | 0.68 | 194.37
2026-08-27T12:35:56 | 0.45 | 194.37
2026-08-27T12:36:01 | 0.45 | 194.37
2026-08-27T12:36:06 | 0.68 | 194.37
2026-08-27T12:36:12 | 0.68 | 194.37
2026-08-27T12:36:17 | 0.91 | 194.37
2026-08-27T12:36:23 | 0.68 | 194.37
2026-08-27T12:36:28 | 0.68 | 194.37
2026-08-27T12:36:34 | 0.46 | 194.37
2026-08-27T12:36:39 | 0.46 | 194.37
2026-08-27T12:36:44 | 0.68 | 194.37
2026-08-27T12:36:49 | 0.9 | 194.37
2026-08-27T12:36:54 | 0.68 | 194.37
2026-08-27T12:37:00 | 0.91 | 194.37
2026-08-27T12:37:05 | 0.9 | 194.37
2026-08-27T12:37:10 | 0.9 | 194.37
2026-08-27T12:37:15 | 0.68 | 193.98
2026-08-27T12:37:20 | 0.68 | 194.37
2026-08-27T12:37:25 | 0.68 | 194.37
2026-08-27T12:37:32 | 0.68 | 194.17
2026-08-27T12:37:38 | 0.68 | 194.37
2026-08-27T12:37:43 | 0.68 | 194.17
2026-08-27T12:37:48 | 0.68 | 194.37
2026-08-27T12:37:53 | 0.68 | 193.98
2026-08-27T12:37:58 | 0.45 | 194.17
2026-08-27T12:38:04 | 0.45 | 194.17
2026-08-27T12:38:09 | 0.68 | 194.37
2026-08-27T12:38:14 | 0.45 | 194.37
2026-08-27T12:38:19 | 0.45 | 194.37
2026-08-27T12:38:24 | 0.45 | 194.37
2026-08-27T12:38:30 | 0.68 | 194.37
2026-08-27T12:38:35 | 0.45 | 194.37
2026-08-27T12:38:40 | 0.45 | 194.37
2026-08-27T12:38:45 | 0.45 | 194.37
2026-08-27T12:38:50 | 0.45 | 194.37
2026-08-27T12:38:55 | 0.45 | 194.37
2026-08-27T12:39:01 | 0.45 | 194.37
2026-08-27T12:39:06 | 0.45 | 194.37
2026-08-27T12:39:11 | 0.45 | 194.37
2026-08-27T12:39:16 | 0.68 | 194.37
2026-08-27T12:39:21 | 0.68 | 194.37
2026-08-27T12:39:27 | 0.68 | 194.37
2026-08-27T12:39:34 | 0.68 | 194.37
2026-08-27T12:39:39 | 0.9 | 194.37
2026-08-27T12:39:44 | 0.68 | 194.37
2026-08-27T12:39:49 | 0.68 | 194.37
2026-08-27T12:39:54 | 0.68 | 194.37
2026-08-27T12:40:00 | 0.68 | 194.37
2026-08-27T12:40:05 | 0.9 | 194.37
2026-08-27T12:40:10 | 0.68 | 194.37
2026-08-27T12:40:15 | 0.68 | 194.37
2026-08-27T12:40:20 | 0.45 | 194.37
2026-08-27T12:40:25 | 0.68 | 194.37
2026-08-27T12:40:31 | 0.68 | 194.37
2026-08-27T12:40:36 | 0.68 | 194.37
2026-08-27T12:40:41 | 0.45 | 194.37
2026-08-27T12:40:46 | 0.45 | 194.37
2026-08-27T12:40:51 | 0.45 | 194.37
2026-08-27T12:40:57 | 0.45 | 194.37
2026-08-27T12:41:02 | 0.45 | 194.37
2026-08-27T12:41:08 | 0.45 | 194.37
2026-08-27T12:41:13 | 0.68 | 194.17
2026-08-27T12:41:18 | 0.68 | 194.37
2026-08-27T12:41:24 | 0.68 | 194.37
2026-08-27T12:41:29 | 0.68 | 194.37
2026-08-27T12:41:34 | 0.68 | 193.98
2026-08-27T12:41:39 | 0.68 | 194.17
2026-08-27T12:41:44 | 0.45 | 194.17
2026-08-27T12:41:49 | 0.68 | 194.37
2026-08-27T12:41:55 | 0.45 | 193.98
2026-08-27T12:42:00 | 0.45 | 193.98
2026-08-27T12:42:05 | 0.45 | 193.98
2026-08-27T12:42:10 | 0.68 | 193.98
2026-08-27T12:42:15 | 0.68 | 194.17
2026-08-27T12:42:20 | 0.68 | 193.98
2026-08-27T12:42:26 | 0.68 | 194.17
2026-08-27T12:42:31 | 0.68 | 194.37
2026-08-27T12:42:36 | 0.68 | 194.37
2026-08-27T12:42:43 | 0.68 | 194.17
2026-08-27T12:42:48 | 0.68 | 193.98
2026-08-27T12:42:53 | 0.9 | 193.98
2026-08-27T12:42:58 | 0.68 | 193.18
2026-08-27T12:43:04 | 0.68 | 193.18
2026-08-27T12:43:09 | 0.68 | 193.18
2026-08-27T12:43:14 | 0.45 | 194.37
2026-08-27T12:43:19 | 0.68 | 87.77
2026-08-27T12:43:24 | 0.68 | 87.82
2026-08-27T12:43:29 | 0.68 | 87.82
2026-08-27T12:43:35 | 0.68 | 87.94
2026-08-27T12:43:40 | 0.68 | 88
2026-08-27T12:43:45 | 0.68 | 88
2026-08-27T12:43:50
2026-08-27T12:44:05 | 0.68 | 194.37
2026-08-27T12:44:10 | 10.11 | 194.37
2026-08-27T12:44:15 | 9.9 | 194.37
2026-08-27T12:44:20 | 10.13 | 194.37
2026-08-27T12:44:26 | 9.91 | 194.37
2026-08-27T12:44:33 | 10.13 | 194.37
2026-08-27T12:44:38 | 9.93 | 194.37
2026-08-27T12:44:43 | 10.13 | 194.37
2026-08-27T12:44:48 | 9.92 | 194.37
2026-08-27T12:44:53 | 10.13 | 194.37
2026-08-27T12:44:59 | 10.15 | 194.37
2026-08-27T12:45:04 | 9.93 | 194.37
2026-08-27T12:45:09 | 10.15 | 194.37
2026-08-27T12:45:14 | 10.35 | 194.37
2026-08-27T12:45:19 | 10.35 | 194.37
2026-08-27T12:45:24 | 10.56 | 194.37
2026-08-27T12:45:30 | 10.35 | 194.37
2026-08-27T12:45:35 | 10.55 | 194.37
2026-08-27T12:45:40 | 10.55 | 194.37
2026-08-27T12:45:45 | 10.55 | 194.37
2026-08-27T12:45:50 | 10.62 | 195.17
2026-08-27T12:45:55 | 10.4 | 194.37
2026-08-27T12:46:01 | 10.19 | 195.17
2026-08-27T12:46:06 | 10.19 | 194.37
2026-08-27T12:46:11 | 10.19 | 194.37
2026-08-27T12:46:16 | 10.2 | 194.37
2026-08-27T12:46:22 | 10.2 | 194.37
2026-08-27T12:46:28 | 10.2 | 194.37
2026-08-27T12:46:33 | 10.19 | 194.37
2026-08-27T12:46:38 | 10.19 | 194.37
2026-08-27T12:46:43 | 10.13 | 194.37
2026-08-27T12:46:48 | 10.35 | 194.37
2026-08-27T12:46:54 | 10.35 | 194.37
2026-08-27T12:47:00 | 10.33 | 194.37
2026-08-27T12:47:05 | 10.33 | 194.37
2026-08-27T12:47:10 | 10.11 | 194.37
2026-08-27T12:47:15 | 10.33 | 194.37
2026-08-27T12:47:21 | 10.11 | 194.37
2026-08-27T12:47:27 | 10.11 | 194.37
2026-08-27T12:47:32 | 10.17 | 194.37
2026-08-27T12:47:37 | 10.17 | 194.37
2026-08-27T12:47:42 | 10.11 | 194.37
2026-08-27T12:47:48 | 10.32 | 194.37
2026-08-27T12:47:54 | 10.11 | 194.37
2026-08-27T12:47:59 | 10.11 | 194.37
2026-08-27T12:48:04 | 10.33 | 194.37
2026-08-27T12:48:09 | 9.91 | 194.37
2026-08-27T12:48:14 | 9.9 | 194.37
2026-08-27T12:48:19 | 10.11 | 194.37
2026-08-27T12:48:25 | 10.11 | 194.37
2026-08-27T12:48:30 | 10.11 | 194.37
2026-08-27T12:48:35 | 9.9 | 194.37
2026-08-27T12:48:40 | 9.9 | 194.37
2026-08-27T12:48:45 | 10.11 | 194.37
2026-08-27T12:48:50 | 10.11 | 194.37
2026-08-27T12:48:56 | 10.11 | 194.37
2026-08-27T12:49:01 | 10.11 | 194.37
2026-08-27T12:49:06 | 10.11 | 194.37
2026-08-27T12:49:11 | 10.11 | 194.37
2026-08-27T12:49:16 | 10.32 | 194.37
2026-08-27T12:49:22 | 10.12 | 194.37
2026-08-27T12:49:27 | 10.12 | 194.37
2026-08-27T12:49:32 | 10.34 | 194.37
2026-08-27T12:49:37 | 10.34 | 194.37
2026-08-27T12:49:42 | 10.13 | 194.37
2026-08-27T12:49:47 | 10.12 | 194.37
2026-08-27T12:49:53 | 10.34 | 194.37
2026-08-27T12:49:58 | 10.35 | 194.37
2026-08-27T12:50:03 | 10.34 | 194.37
2026-08-27T12:50:08 | 10.34 | 194.37
2026-08-27T12:50:14 | 10.35 | 194.37
2026-08-27T12:50:19 | 10.55 | 194.37
2026-08-27T12:50:25 | 10.34 | 194.37
2026-08-27T12:50:30 | 10.55 | 194.17
2026-08-27T12:50:35 | 10.32 | 194.17
2026-08-27T12:50:40 | 10.34 | 194.37
2026-08-27T12:50:45 | 10.55 | 194.17
2026-08-27T12:50:50 | 10.33 | 194.17
2026-08-27T12:50:56 | 10.33 | 194.17
2026-08-27T12:51:01 | 10.32 | 194.17
2026-08-27T12:51:06 | 10.12 | 194.17
2026-08-27T12:51:11 | 10.32 | 194.17
2026-08-27T12:51:16 | 10.32 | 193.98
2026-08-27T12:51:22 | 10.32 | 194.17
2026-08-27T12:51:27 | 10.32 | 193.98
2026-08-27T12:51:33 | 10.33 | 193.98
2026-08-27T12:51:38 | 10.34 | 194.17
2026-08-27T12:51:44 | 10.55 | 194.17
2026-08-27T12:51:49 | 10.55 | 194.17
2026-08-27T12:51:54 | 10.34 | 194.17
2026-08-27T12:51:59 | 10.34 | 194.17
2026-08-27T12:52:04 | 10.54 | 193.98
2026-08-27T12:52:09 | 10.32 | 193.98
2026-08-27T12:52:15 | 10.32 | 193.98
2026-08-27T12:52:20 | 10.32 | 193.98
2026-08-27T12:52:25 | 10.32 | 193.98
2026-08-27T12:52:30 | 10.53 | 193.98
2026-08-27T12:52:35 | 10.31 | 193.18
2026-08-27T12:52:40 | 10.31 | 193.18
2026-08-27T12:52:46 | 10.32 | 193.98
2026-08-27T12:52:51 | 10.31 | 193.18
2026-08-27T12:52:56 | 10.31 | 193.18
2026-08-27T12:53:01 | 0.9 | 193.18
2026-08-27T12:53:06 | 0.9 | 193.18
2026-08-27T12:53:11 | 0.68 | 193.18
2026-08-27T12:53:17 | 0.68 | 193.18
2026-08-27T12:53:22 | 0.9 | 193.18
2026-08-27T12:53:27 | 0.9 | 193.18
2026-08-27T12:53:32 | 0.68 | 193.18
2026-08-27T12:53:37 | 0.9 | 193.18
2026-08-27T12:53:43 | 0.67 | 193.18
2026-08-27T12:53:48 | 0.45 | 193.18
2026-08-27T12:53:53 | 0.45 | 193.18
2026-08-27T12:53:58 | 0.67 | 193.18
2026-08-27T12:54:03 | 0.67 | 193.18
2026-08-27T12:54:08 | 0.67 | 193.18
2026-08-27T12:54:14 | 0.67 | 193.18
2026-08-27T12:54:20 | 0.67 | 193.18
2026-08-27T12:54:25 | 0.67 | 193.18
2026-08-27T12:54:30 | 0.67 | 193.18
2026-08-27T12:54:35 | 0.67 | 193.18
2026-08-27T12:54:41 | 0.67 | 193.18
2026-08-27T12:54:46 | 0.67 | 193.18
2026-08-27T12:54:51 | 0.45 | 193.18
2026-08-27T12:54:56 | 0.67 | 193.18
2026-08-27T12:55:01 | 0.9 | 193.18
2026-08-27T12:55:06 | 0.67 | 193.18
2026-08-27T12:55:12 | 0.45 | 193.18
2026-08-27T12:55:17 | 0.45 | 193.18
2026-08-27T12:55:22 | 0.45 | 193.18
2026-08-27T12:55:27 | 0.67 | 193.18
2026-08-27T12:55:32 | 0.45 | 193.18
2026-08-27T12:55:38 | 0.45 | 193.18
2026-08-27T12:55:44 | 0.45 | 193.18
2026-08-27T12:55:49 | 0.45 | 193.18
2026-08-27T12:55:54 | 0.45 | 193.18
2026-08-27T12:55:59 | 0.67 | 193.18
2026-08-27T12:56:05 | 0.45 | 193.18
2026-08-27T12:56:11 | 0.67 | 193.18
2026-08-27T12:56:16 | 0.67 | 193.18
2026-08-27T12:56:21 | 0.67 | 193.18
2026-08-27T12:56:26 | 0.67 | 193.18
2026-08-27T12:56:31 | 0.67 | 193.18
2026-08-27T12:56:39 | 0.89 | 193.18
2026-08-27T12:56:45 | 0.67 | 193.18
2026-08-27T12:56:50 | 0.45 | 193.18
2026-08-27T12:56:55 | 0.45 | 193.18
2026-08-27T12:57:00 | 0.67 | 193.18
2026-08-27T12:57:06 | 0.67 | 193.18
2026-08-27T12:57:11 | 0.67 | 192.99
2026-08-27T12:57:16 | 0.67 | 192.99
2026-08-27T12:57:21 | 0.67 | 192.99
2026-08-27T12:57:26 | 0.67 | 192.79
2026-08-27T12:57:34 | 0.89 | 192.79
2026-08-27T12:57:39 | 0.67 | 192.99
2026-08-27T12:57:44 | 0.89 | 192.79
2026-08-27T12:57:49 | 0.89 | 192.99
2026-08-27T12:57:54 | 0.89 | 192.79
2026-08-27T12:57:59 | 0.67 | 192.79
2026-08-27T12:58:05 | 0.67 | 192.79
2026-08-27T12:58:10 | 0.67 | 192.79
2026-08-27T12:58:15 | 0.67 | 192.79
2026-08-27T12:58:20 | 0.67 | 192.79
2026-08-27T12:58:25 | 0.67 | 192.79
2026-08-27T12:58:30 | 0.44 | 192.79
2026-08-27T12:58:36 | 0.67 | 192
2026-08-27T12:58:41 | 0.44 | 192
2026-08-27T12:58:46 | 0.44 | 192
2026-08-27T12:58:51 | 0.67 | 192
2026-08-27T12:58:56 | 0.67 | 192
2026-08-27T12:59:01 | 0.67 | 192
2026-08-27T12:59:07 | 0.67 | 192
2026-08-27T12:59:12 | 0.67 | 192
2026-08-27T12:59:17 | 0.67 | 192
2026-08-27T12:59:22 | 0.66 | 192
2026-08-27T12:59:27 | 0.66 | 192
2026-08-27T12:59:33 | 0.66 | 192
2026-08-27T12:59:38 | 0.66 | 192
2026-08-27T12:59:43 | 0.66 | 192
2026-08-27T12:59:48 | 0.66 | 192
2026-08-27T12:59:53 | 0.66 | 192
2026-08-27T12:59:58 | 0.66 | 192
2026-08-27T13:00:04 | 0.67 | 192
2026-08-27T13:00:09 | 0.67 | 192
2026-08-27T13:00:14 | 0.66 | 192
2026-08-27T13:00:19 | 0.89 | 192
2026-08-27T13:00:24 | 0.89 | 192
2026-08-27T13:00:30 | 0.89 | 192
2026-08-27T13:00:35 | 28.93 | 193.98
2026-08-27T13:00:40 | 2.7 | 194.17
2026-08-27T13:00:45 | 15.89 | 193.98
2026-08-27T13:00:50 | 22.35 | 193.98
2026-08-27T13:00:55 | 22.38 | 194.17
2026-08-27T13:01:01 | 15.24 | 194.37
2026-08-27T13:01:07 | 32.81 | 195.56
2026-08-27T13:01:12 | 76.7 | 195.56
2026-08-27T13:01:17 | 4.66 | 195.56
2026-08-27T13:01:23 | 0.64 | 195.56
2026-08-27T13:01:28 | 0.69 | 195.56
2026-08-27T13:01:33 | 0.69 | 195.56
2026-08-27T13:01:38 | 0.46 | 195.56
2026-08-27T13:01:43 | 0.46 | 195.56
2026-08-27T13:01:49 | 0.69 | 195.56
2026-08-27T13:01:54 | 0.69 | 195.56
2026-08-27T13:02:01 | 0.69 | 195.56
2026-08-27T13:02:06 | 0.69 | 195.56
2026-08-27T13:02:11 | 0.46 | 195.56
2026-08-27T13:02:16 | 0.69 | 195.56
2026-08-27T13:02:21 | 0.46 | 195.56
2026-08-27T13:02:26 | 0.46 | 195.56
2026-08-27T13:02:32 | 0.92 | 195.56
2026-08-27T13:02:37 | 0.69 | 195.56
2026-08-27T13:02:42 | 0.92 | 195.56
2026-08-27T13:02:47 | 0.69 | 195.56
2026-08-27T13:02:52 | 0.92 | 195.56
2026-08-27T13:02:58 | 0.92 | 195.56
2026-08-27T13:03:03 | 0.69 | 195.56
2026-08-27T13:03:08 | 0.69 | 195.56
2026-08-27T13:03:13 | 0.69 | 195.56
2026-08-27T13:04:47 | 0.46 | 195.56
2026-08-27T13:04:52 | 0.46 | 195.56
2026-08-27T13:04:58 | 0.69 | 195.56
2026-08-27T13:05:03 | 0.46 | 195.56
2026-08-27T13:05:08 | 0.69 | 195.56
2026-08-27T13:05:13 | 0.69 | 195.56
2026-08-27T13:05:18 | 0.46 | 195.56
2026-08-27T13:05:24 | 0.69 | 195.56
2026-08-27T13:05:29 | 0.46 | 195.56
2026-08-27T13:05:34 | 0.46 | 195.56
2026-08-27T13:05:39 | 0.69 | 195.56
2026-08-27T13:05:44 | 0.92 | 195.56
2026-08-27T13:05:49 | 0.69 | 195.56
2026-08-27T13:05:55 | 0.69 | 195.56
2026-08-27T13:06:00 | 0.69 | 195.56
2026-08-27T13:06:06 | 0.46 | 195.56
2026-08-27T13:06:12 | 0.69 | 195.56
2026-08-27T13:06:17 | 0.92 | 195.56
2026-08-27T13:06:22 | 0.92 | 195.56
2026-08-27T13:06:28 | 0.92 | 195.56
2026-08-27T13:06:33 | 0.92 | 195.56
2026-08-27T13:06:39 | 0.92 | 195.56
2026-08-27T13:06:44 | 0.69 | 195.56
2026-08-27T13:06:49 | 0.92 | 195.56
2026-08-27T13:06:55 | 0.69 | 195.56
2026-08-27T13:07:00 | 0.92 | 195.56
2026-08-27T13:07:05 | 0.92 | 195.56
2026-08-27T13:07:10 | 0.46 | 195.56
2026-08-27T13:07:15 | 0.69 | 195.56
2026-08-27T13:07:20 | 0.46 | 195.56
2026-08-27T13:07:26 | 0.46 | 195.56
2026-08-27T13:07:31 | 0.46 | 195.56
2026-08-27T13:07:35 | 0.46 | 195.56
2026-08-27T13:09:04 | 0.46 | 195.56
2026-08-27T13:09:09 | 0.69 | 195.56
2026-08-27T13:09:14 | 0.69 | 195.56
2026-08-27T13:09:19 | 0.69 | 195.56
2026-08-27T13:09:24 | 0.69 | 195.56
2026-08-27T13:09:29 | 0.69 | 195.56
2026-08-27T13:09:35 | 0.92 | 195.56
2026-08-27T13:09:40 | 0.69 | 195.56
2026-08-27T13:09:45 | 0.69 | 195.56
2026-08-27T13:09:50 | 0.69 | 195.56
2026-08-27T13:09:55 | 0.92 | 195.56
2026-08-27T13:10:01 | 0.92 | 195.56
2026-08-27T13:10:07 | 0.92 | 195.56
2026-08-27T13:10:12 | 1.15 | 195.56
2026-08-27T13:10:17 | 0.92 | 195.56
2026-08-27T13:10:22 | 0.69 | 195.56
2026-08-27T13:10:28 | 0.92 | 195.56
2026-08-27T13:10:33 | 0.92 | 195.56
2026-08-27T13:10:38 | 0.92 | 195.56
2026-08-27T13:10:43 | 0.92 | 195.56
2026-08-27T13:10:48 | 0.92 | 195.56
2026-08-27T13:10:53 | 0.92 | 195.56
2026-08-27T13:10:59 | 0.92 | 195.56
2026-08-27T13:11:04 | 0.69 | 195.56
2026-08-27T13:11:09 | 0.92 | 195.56
2026-08-27T13:11:14 | 0.69 | 195.56
2026-08-27T13:11:19 | 0.69 | 195.56
2026-08-27T13:11:24 | 0.69 | 195.56
2026-08-27T13:11:30 | 0.69 | 195.56
2026-08-27T13:11:35 | 0.69 | 195.56
2026-08-27T13:11:40 | 0.46 | 195.56
2026-08-27T13:11:45 | 0.46 | 195.56
2026-08-27T13:11:50 | 0.46 | 195.56
2026-08-27T13:11:56 | 0.69 | 196.36
2026-08-27T13:12:01 | 0.46 | 196.36
2026-08-27T13:12:06 | 0.69 | 195.56
2026-08-27T13:12:11 | 0.46 | 196.36
2026-08-27T13:12:16 | 0.46 | 195.56
2026-08-27T13:12:21 | 0.46 | 196.36
2026-08-27T13:12:27 | 0.46 | 196.36
2026-08-27T13:12:32 | 0.46 | 196.36
2026-08-27T13:12:38 | 0.46 | 196.36
2026-08-27T13:12:43 | 0.46 | 196.36
2026-08-27T13:12:48 | 0.46 | 196.36
2026-08-27T13:12:53 | 0.46 | 196.36
2026-08-27T13:12:59 | 0.46 | 196.36
2026-08-27T13:13:04 | 0.46 | 196.36
2026-08-27T13:13:10 | 0.46 | 195.56
2026-08-27T13:13:15 | 0.46 | 196.36
2026-08-27T13:13:20 | 0.69 | 195.56
2026-08-27T13:13:27 | 0.69 | 195.56
2026-08-27T13:13:33 | 0.46 | 196.36
2026-08-27T13:13:38 | 0.46 | 196.36
2026-08-27T13:13:43 | 0.46 | 195.56
2026-08-27T13:13:48 | 0.69 | 195.56
2026-08-27T13:13:54 | 0.69 | 195.56
2026-08-27T13:13:59 | 0.46 | 195.56
2026-08-27T13:14:04 | 0.46 | 196.36
2026-08-27T13:14:09 | 0.46 | 195.56
2026-08-27T13:14:14 | 0.46 | 196.36
2026-08-27T13:14:19 | 0.46 | 196.36
2026-08-27T13:14:25 | 0.46 | 196.36
2026-08-27T13:14:30 | 0.46 | 196.36
2026-08-27T13:14:35 | 0.69 | 196.36
2026-08-27T13:14:40 | 0.69 | 196.36
2026-08-27T13:14:45 | 0.69 | 196.36
2026-08-27T13:14:50 | 0.93 | 196.36
2026-08-27T13:14:56 | 0.7 | 196.36
2026-08-27T13:15:01 | 0.69 | 196.36
2026-08-27T13:15:06 | 0.69 | 196.36
2026-08-27T13:15:11 | 0.69 | 196.36
2026-08-27T13:15:16 | 0.46 | 196.36
2026-08-27T13:15:21 | 0.46 | 196.36
2026-08-27T13:15:27 | 0.69 | 196.36
2026-08-27T13:15:32 | 0.69 | 196.36
2026-08-27T13:15:37 | 0.69 | 196.36
2026-08-27T13:15:42 | 0.69 | 196.36
2026-08-27T13:15:47 | 0.69 | 196.36
2026-08-27T13:15:53 | 0.69 | 196.36
2026-08-27T13:15:58 | 0.7 | 196.56
2026-08-27T13:16:05 | 0.7 | 196.56
2026-08-27T13:16:10 | 0.93 | 196.36
2026-08-27T13:16:16 | 0.7 | 196.36
2026-08-27T13:16:22 | 0.93 | 196.36
2026-08-27T13:16:27 | 0.93 | 196.56
2026-08-27T13:16:38 | 0.93 | 196.36
2026-08-27T13:16:43 | 0.7 | 196.76
2026-08-27T13:16:49 | 0.7 | 196.56
2026-08-27T13:16:54 | 0.7 | 196.56
2026-08-27T13:17:00 | 0.7 | 196.76
2026-08-27T13:20:11 | 0.23 | 196.76
2026-08-27T13:20:23 | 0.23 | 196.76
2026-08-27T13:20:28 | 0.23 | 196.76
2026-08-27T13:20:38 | 0.23 | 196.76
2026-08-27T13:20:43 | 0.23 | 196.76
2026-08-27T13:21:39 | 0.47 | 196.76
2026-08-27T13:21:44 | 0.7 | 196.76
2026-08-27T13:28:37 | 0.47 | 197.57
2026-08-27T13:28:46 | 0.47 | 197.57
2026-08-27T13:28:56 | 0.47 | 197.57
2026-08-27T13:29:07 | 0.47 | 197.57
2026-08-27T13:29:12 | 0.23 | 197.57
2026-08-27T13:29:17 | 0.47 | 197.77
2026-08-27T13:29:27 | 0.23 | 197.77
2026-08-27T13:29:32 | 0.47 | 197.97
2026-08-27T13:29:37 | 0.47 | 197.97
2026-08-27T13:29:42 | 0.47 | 197.97
2026-08-27T13:29:47 | 0.47 | 197.97
2026-08-27T13:29:54 | 0.47 | 197.97
2026-08-27T13:29:59 | 0.47 | 197.97
2026-08-27T13:30:04 | 0.47 | 197.97
2026-08-27T13:30:09 | 0.47 | 197.97
2026-08-27T13:30:14 | 0.47 | 197.97
2026-08-27T13:30:21 | 0.47 | 197.97
2026-08-27T13:30:26 | 0.47 | 197.97
2026-08-27T13:30:31 | 0.47 | 197.97
2026-08-27T13:30:36 | 0.47 | 197.97
2026-08-27T13:30:41 | 0.47 | 197.97
2026-08-27T13:30:46 | 0.47 | 197.97
2026-08-27T13:30:52 | 0.71 | 197.97
2026-08-27T13:30:57 | 0.47 | 197.97
2026-08-27T13:31:02 | 0.71 | 197.97
2026-08-27T13:31:07 | 0.71 | 197.97
2026-08-27T13:31:12 | 0.94 | 197.97
2026-08-27T13:31:29 | 0.71 | 197.97
2026-08-27T13:31:38 | 0.71 | 197.97
2026-08-27T13:31:53 | 0.47 | 197.97
2026-08-27T13:31:58 | 0.71 | 197.97
2026-08-27T13:32:04 | 0.47 | 197.97
2026-08-27T13:32:10 | 0.47 | 197.97
2026-08-27T13:32:15 | 0.47 | 197.97
2026-08-27T13:32:20 | 0.47 | 197.97
2026-08-27T13:32:26 | 0.47 | 197.97
2026-08-27T13:32:31 | 0.71 | 197.97
2026-08-27T13:32:40 | 0.47 | 197.97
2026-08-27T13:32:46 | 0.47 | 197.97
2026-08-27T13:32:51 | 0.47 | 197.97
2026-08-27T13:32:56 | 0.47 | 197.97
2026-08-27T13:33:03 | 0.47 | 197.97
2026-08-27T13:33:08 | 0.47 | 197.97
2026-08-27T13:33:13 | 0.47 | 197.97
2026-08-27T13:33:18 | 0.47 | 197.97
2026-08-27T13:33:23 | 0.47 | 197.97
2026-08-27T13:33:29 | 0.47 | 197.97
2026-08-27T13:33:34 | 0.24 | 197.97
2026-08-27T13:33:39 | 0.47 | 197.97
2026-08-27T13:33:44 | 0.47 | 197.97
2026-08-27T13:33:49 | 0.47 | 197.97
2026-08-27T13:33:54 | 0.47 | 197.97
2026-08-27T13:34:00 | 0.47 | 197.97
2026-08-27T13:34:05 | 0.47 | 197.97
2026-08-27T13:34:10 | 0.47 | 197.97
2026-08-27T13:34:15 | 0.47 | 197.97
2026-08-27T13:34:21 | 0.47 | 197.97
2026-08-27T13:34:26 | 0.24 | 198.78
2026-08-27T13:34:37 | 0 | 198.78
2026-08-27T13:34:42 | 0.47 | 198.78
2026-08-27T13:34:47 | 0.47 | 198.78
2026-08-27T13:34:52 | 0.47 | 197.97
2026-08-27T13:34:57 | 0.47 | 197.97
2026-08-27T13:35:07 | 0.47 | 197.97
2026-08-27T13:35:12 | 0.47 | 197.97
2026-08-27T13:35:18 | 0.47 | 197.97
2026-08-27T13:35:32 | 0.71 | 197.97
2026-08-27T13:35:42 | 0.95 | 197.97
2026-08-27T13:35:48 | 0.71 | 197.97
2026-08-27T13:35:53 | 0.71 | 197.97
2026-08-27T13:36:03 | 0.47 | 197.97
2026-08-27T13:36:08 | 0.47 | 198.78
2026-08-27T13:40:18 | 0.24 | 198.78
2026-08-27T13:40:23 | 0.48 | 198.98
2026-08-27T13:40:28 | 0.48 | 198.98
2026-08-27T14:39:15 |  | 315.79
2026-08-27T14:39:20 |  | 315.79
2026-08-27T14:39:25 |  | 315.79
2026-08-27T14:39:31 |  | 315.79
2026-08-27T14:39:36 |  | 315.79
2026-08-27T14:39:41 |  | 315.79
2026-08-27T14:39:50 |  | 315.79
2026-08-27T14:40:01 |  | 315.79
2026-08-27T14:40:06 |  | 315.79
2026-08-27T14:40:11 |  | 315.79
2026-08-27T14:40:16 |  | 315.79
2026-08-27T14:40:21 |  | 315.79
2026-08-27T14:40:26 |  | 315.79
2026-08-27T15:24:55
2026-08-27T15:25:26 |  | 315.79
2026-08-27T15:25:31
2026-08-27T15:25:44 |  | 315.79
2026-08-27T15:25:50 |  | 315.79
2026-08-27T15:26:00 |  | 315.79
2026-08-27T15:26:10 | 0 | 315.79
2026-08-27T15:26:16 | 0 | 315.79
2026-08-27T15:26:21 | 0 | 315.79
2026-08-27T15:26:27 | 0 | 315.79
2026-08-27T15:26:32 | 0 | 315.79
2026-08-27T15:26:37 | 0.23 | 315.79
2026-08-27T15:26:43 | 0 | 315.79
2026-08-27T15:26:50 | 0.23 | 315.79
2026-08-27T15:26:55 | 0.23 | 315.79
2026-08-27T15:27:05 | 0.23 | 315.79
2026-08-27T15:27:11 | 0.46 | 315.79
2026-08-27T15:27:16 |  | 315.79
2026-08-27T15:27:21 |  | 315.79
2026-08-27T15:27:26 |  | 315.79
2026-08-27T15:27:31 |  | 315.79
2026-08-27T15:27:36 |  | 315.79
2026-08-27T15:27:42 |  | 315.79
2026-08-27T15:27:47 |  | 315.79
2026-08-27T15:27:52 |  | 315.79
2026-08-27T15:27:57 |  | 315.79
2026-08-27T15:28:02 |  | 315.79
2026-08-27T15:28:07 |  | 315.79
2026-08-27T15:28:13 |  | 315.79
2026-08-27T15:28:18 |  | 315.79
2026-08-27T15:28:23 |  | 315.79
2026-08-27T15:28:28 |  | 315.79
2026-08-27T15:28:33 |  | 315.79
2026-08-27T15:28:40 |  | 315.79
2026-08-27T15:28:45 |  | 315.79
2026-08-27T15:28:50 |  | 315.79
2026-08-27T15:28:56 |  | 315.79
2026-08-27T15:29:01 |  | 315.79
2026-08-27T15:29:06 |  | 315.79
2026-08-27T15:29:12 |  | 315.79
2026-08-27T15:29:17 | 0.23 | 315.79
2026-08-27T15:29:22 | 0.23 | 315.79
2026-08-27T15:29:27 | 0.46 | 315.79
2026-08-27T15:29:32 | 0.23 | 315.79
2026-08-27T15:29:37 | 0.23 | 315.79
2026-08-27T15:29:43 | 0.23 | 315.79
2026-08-27T15:29:48 | 0.23 | 315.79
2026-08-27T15:29:53 | 0.46 | 315.79
2026-08-27T15:29:58 | 0.23 | 315.79
2026-08-27T15:30:03 | 0.23 | 315.79
2026-08-27T15:30:08 | 0.23 | 315.79
2026-08-27T15:30:14 | 0.23 | 315.79
2026-08-27T15:30:19 | 0.46 | 315.79
2026-08-27T15:30:24 | 0.23 | 315.79
2026-08-27T15:30:29 | 0.46 | 315.79
2026-08-27T15:30:34 | 0.23 | 315.79
2026-08-27T15:30:39 | 0.23 | 315.79
2026-08-27T15:30:45 | 0.46 | 315.79
2026-08-27T15:30:50 | 0.23 | 315.79
2026-08-27T15:30:55 | 0.23 | 315.79
2026-08-27T15:31:00 | 0.23 | 315.79
2026-08-27T15:31:05 | 0.23 | 315.79
2026-08-27T15:31:10 | 0 | 315.79
2026-08-27T15:31:16 | 0.23 | 315.79
2026-08-27T15:31:21 | 0.23 | 315.79
2026-08-27T15:31:26 | 0.23 | 315.79
2026-08-27T15:31:31 |  | 315.79
2026-08-27T15:31:36 |  | 315.79
2026-08-27T15:31:42 |  | 315.79
2026-08-27T15:31:48 |  | 315.79
2026-08-27T15:31:53 |  | 315.79
2026-08-27T15:31:58 |  | 315.79
2026-08-27T15:32:03 |  | 315.79
2026-08-27T15:32:08 |  | 315.79
2026-08-27T15:32:15 |  | 315.79
2026-08-27T15:32:20 |  | 315.79
2026-08-27T15:32:25 |  | 315.79
2026-08-27T15:32:31 |  | 315.79
2026-08-27T15:32:38 |  | 315.79
2026-08-27T15:32:43 |  | 315.79
2026-08-27T15:32:48 | 0.46 | 315.79
2026-08-27T15:32:53 | 0.46 | 315.79
2026-08-27T15:32:58 | 0.46 | 257.94
2026-08-27T15:33:03 | 0.23 | 195.56
2026-08-27T15:33:09 | 0.46 | 195.36
2026-08-27T15:33:14 | 0.23 | 195.56
2026-08-27T15:33:19 | 0.45 | 195.56
2026-08-27T15:33:24 | 0.23 | 195.56
2026-08-27T15:33:30 | 0.23 | 195.56
2026-08-27T15:33:36 | 0.23 | 195.56
2026-08-27T15:33:41 | 0.23 | 195.56
2026-08-27T15:33:46 | 0.46 | 195.56
2026-08-27T15:33:52 | 0.46 | 195.56
2026-08-27T15:33:58 | 0.23 | 195.56
2026-08-27T15:34:03 | 0.45 | 195.56
2026-08-27T15:34:11 | 0.45 | 195.17
2026-08-27T15:34:16 | 0.45 | 195.17
2026-08-27T15:34:21 | 0.45 | 195.17
2026-08-27T15:34:26 | 0.45 | 195.17
2026-08-27T15:34:31 | 0.45 | 194.37
2026-08-27T15:34:36 | 0.45 | 195.17
2026-08-27T15:34:42 | 0.23 | 195.17
2026-08-27T15:34:47 | 0.45 | 195.17
2026-08-27T15:34:52 | 0.23 | 195.17
2026-08-27T15:34:57 | 0.23 | 195.17
2026-08-27T15:35:02 | 0.23 | 195.17
2026-08-27T15:35:07 | 0.23 | 195.17
2026-08-27T15:35:13 | 0.23 | 195.56
2026-08-27T15:35:18 | 0.23 | 195.36
2026-08-27T15:35:23 | 0.23 | 195.17
2026-08-27T15:35:28 | 0.23 | 195.17
2026-08-27T15:35:34 | 0.23 | 195.17
2026-08-27T15:35:41 | 0.45 | 195.17
2026-08-27T15:35:46 | 0 | 195.17
2026-08-27T15:35:51 | 0 | 195.36
2026-08-27T15:35:57 | 0.23 | 195.36
2026-08-27T15:36:02 | 0 | 195.36
2026-08-27T15:36:08 | 0.23 | 195.56
2026-08-27T15:36:13 | 0 | 195.56
2026-08-27T15:36:18 | 0.23 | 195.56
2026-08-27T15:36:23 | 0 | 195.56
2026-08-27T15:36:29 | 0 | 195.56
2026-08-27T15:36:34 | 0.23 | 195.56
2026-08-27T15:36:40 | 0.23 | 195.36
2026-08-27T15:36:45 | 0.45 | 195.36
2026-08-27T15:36:50 | 0.23 | 195.36
2026-08-27T15:36:55 | 0.23 | 195.56
2026-08-27T15:37:01 | 0.45 | 195.56
2026-08-27T15:37:08 | 0.23 | 195.36
2026-08-27T15:37:13 | 0.23 | 195.36
2026-08-27T15:37:18 | 0.23 | 195.36
2026-08-27T15:37:24 | 0.23 | 195.56
2026-08-27T15:37:30 | 0.23 | 195.56
2026-08-27T15:37:35 | 0.23 | 195.56
2026-08-27T15:37:41 | 0.23 | 195.56
2026-08-27T15:37:46 | 0.23 | 195.56
2026-08-27T15:37:53 | 0.23 | 195.56
2026-08-27T15:37:58 | 0.23 | 315.79
2026-08-27T15:38:08 |  | 315.79
2026-08-27T15:38:23 | 0.23 | 315.79
2026-08-27T15:38:28 | 0.46 | 315.79
2026-08-27T15:38:33 | 0.23 | 315.79
2026-08-27T15:38:38 | 0 | 315.79
2026-08-27T15:38:53 | 0.23 | 315.79
2026-08-27T15:40:02 | 0 | 315.79
2026-08-27T15:40:08 | 0.23 | 315.79
2026-08-27T15:40:13 | 0.23 | 315.79
2026-08-27T15:40:18 | 0.23 | 315.79
2026-08-27T15:40:23 | 0.23 | 315.79
2026-08-27T15:40:28 | 0.46 | 315.79
2026-08-27T15:40:38 | 0.23 | 315.79
2026-08-27T15:40:48 | 0.46 | 315.79
2026-08-27T15:40:54 | 0.23 | 315.79
2026-08-27T15:40:59 | 0.23 | 315.79
2026-08-27T15:41:05 | 0.23 | 315.79
2026-08-27T15:41:10 | 0.23 | 315.79
2026-08-27T15:41:15 | 0.23 | 315.79
2026-08-27T15:41:20 | 0.46 | 315.79
2026-08-27T15:41:25 | 0.46 | 315.79
2026-08-27T15:41:31 | 0.23 | 315.79
2026-08-27T15:41:36 | 0.23 | 315.79
2026-08-27T15:41:42 | 0.23 | 315.79
2026-08-27T15:41:47 | 0.46 | 315.79
2026-08-27T15:41:52 | 0.23 | 315.79
2026-08-27T15:41:59 | 0.23 | 315.79
2026-08-27T15:42:05 | 0.46 | 315.79
2026-08-27T15:42:11 | 0.23 | 315.79
2026-08-27T15:42:16 | 0.46 | 315.79
2026-08-27T15:42:22 | 0.46 | 315.79
2026-08-27T15:42:27 | 0.46 | 315.79
2026-08-27T15:42:32 | 0.46 | 315.79
2026-08-27T15:42:37 | 0.23 | 315.79
2026-08-27T15:42:42 | 0.46 | 315.79
2026-08-27T15:42:47 | 0.23 | 315.79
2026-08-27T15:42:54 | 0.23 | 315.79
2026-08-27T15:42:59 | 0.23 | 315.79
2026-08-27T15:43:04 | 0 | 315.79
2026-08-27T15:43:07 | 0 | 315.79
2026-08-27T15:43:17 | 0 | 315.79
2026-08-27T15:43:33 | 0 | 315.79
2026-08-27T15:43:38 | 0 | 315.79
2026-08-27T15:43:43 | 0 | 315.79
2026-08-27T15:43:48 | 0 | 315.79
2026-08-27T15:43:53 | 0.23 | 315.79
2026-08-27T15:43:59 | 0.23 | 315.79
2026-08-27T15:44:04 | 0.23 | 315.79
2026-08-27T15:44:09 | 0.23 | 315.79
2026-08-27T15:44:14 | 0 | 315.79
2026-08-27T15:44:19 | 0 | 315.79
2026-08-27T15:44:25 | 0.45 | 315.79
2026-08-27T15:44:30 | 0.45 | 315.79
2026-08-27T15:44:35 | 0.45 | 315.79
2026-08-27T15:44:40 | 0.23 | 315.79
2026-08-27T15:44:45 | 0.23 | 315.79
2026-08-27T15:44:50 | 0.23 | 315.79
2026-08-27T15:44:56 | 0.23 | 315.79
2026-08-27T15:45:01 | 0.23 | 315.79
2026-08-27T15:45:06 | 0.45 | 315.79
2026-08-27T15:45:11 | 0.23 | 315.79
2026-08-27T15:45:16 | 0.45 | 315.79
2026-08-27T15:45:22 | 0.45 | 315.79
2026-08-27T15:45:27 | 0.45 | 315.79
2026-08-27T15:45:32 | 0.45 | 315.79
2026-08-27T15:45:37 | 0.23 | 315.79
2026-08-27T15:45:42 | 0.45 | 315.79
2026-08-27T15:45:48 | 0.45 | 315.79
2026-08-27T15:45:53 | 0.23 | 315.79
2026-08-27T15:45:58 | 0.23 | 315.79
2026-08-27T15:46:03 | 0.23 | 315.79
2026-08-27T15:46:08 | 0.45 | 315.79
2026-08-27T15:46:13 | 0.45 | 315.79
2026-08-27T15:46:19 | 0.45 | 315.79
2026-08-27T15:46:24 | 0.23 | 315.79
2026-08-27T15:46:29 | 0.23 | 315.79
2026-08-27T15:46:36 | 0.23 | 315.79
2026-08-27T15:46:42 | 0.23 | 315.79
2026-08-27T15:46:47 | 0.23 | 315.79
2026-08-27T15:46:52 | 0.45 | 315.79
2026-08-27T15:46:57 | 0.46 | 315.79
2026-08-27T15:47:02 |  | 315.79
2026-08-27T15:47:37 |  | 315.79
2026-08-27T15:47:42 |  | 315.79
2026-08-27T15:47:52 |  | 315.79
2026-08-27T15:47:57 | 0.23 | 315.79
2026-08-27T15:48:03 | 0.46 | 315.79
2026-08-27T15:48:13 | 0.23 | 315.79
2026-08-27T15:48:23 | 0.23 | 315.79
2026-08-27T15:48:28 | 0.23 | 315.79
2026-08-27T15:48:33 | 0.23 | 315.79
2026-08-27T15:48:38 | 0.23 | 315.79
2026-08-27T15:48:44 | 0 | 315.79
2026-08-27T15:48:49 | 0.23 | 315.79
2026-08-27T15:48:55 | 0.23 | 315.79
2026-08-27T15:49:00 | 0.23 | 315.79
2026-08-27T15:49:05 | 0.46 | 315.79
2026-08-27T15:49:10 | 0.23 | 315.79
2026-08-27T15:49:15 | 0.23 | 315.79
2026-08-27T15:49:20 | 0.23 | 315.79
2026-08-27T15:49:40 | 0.23 | 315.79
2026-08-27T15:49:45 | 0.23 | 315.79
2026-08-27T15:49:54 | 0.23 | 315.79
2026-08-27T15:50:04 | 0.23 | 315.79
2026-08-27T15:50:09 | 0.23 | 315.79
2026-08-27T15:50:14 | 0.23 | 315.79
2026-08-27T15:50:20 | 0 | 315.79
2026-08-27T15:50:25 | 0 | 315.79
2026-08-27T15:50:30 | 0 | 315.79
2026-08-27T15:50:35 | 0.23 | 315.79
2026-08-27T15:50:40 | 0.23 | 315.79
2026-08-27T15:50:45 | 0.23 | 315.79
2026-08-27T15:55:27 | 0.23 | 315.79
2026-08-27T15:55:32 | 0 | 315.79
2026-08-27T15:55:37 | 0.23 | 315.79
2026-08-27T15:55:44 | 0.46 | 315.79
2026-08-27T15:55:49 | 0.46 | 315.79
2026-08-27T15:55:54
2026-08-27T15:57:06 | 0.69 | 315.79
2026-08-27T15:57:16 | 0.46 | 315.79
2026-08-27T15:57:22 | 0.46 | 315.79
2026-08-27T15:57:27 | 0.46 | 315.79
2026-08-27T15:57:32 | 0.46 | 315.79
2026-08-27T15:57:37 | 0.46 | 315.79
2026-08-27T15:57:42 | 0.46 | 315.79
2026-08-27T15:57:47 | 0.46 | 315.79
2026-08-27T15:57:52 | 0.46 | 315.79
2026-08-27T15:57:58 | 0.46 | 315.79
2026-08-27T15:58:03 | 0.46 | 315.79
2026-08-27T15:58:08 | 0.46 | 315.79
2026-08-27T15:58:13 | 0.46 | 315.79
2026-08-27T15:58:18 | 0.46 | 315.79
2026-08-27T15:58:23 | 0.23 | 315.79
2026-08-27T15:58:29 | 0.23 | 315.79
2026-08-27T15:58:34 | 0.23 | 315.79
2026-08-27T15:58:39 | 0.23 | 315.79
2026-08-27T15:58:44 | 0.23 | 315.79
2026-08-27T15:58:49 | 0.23 | 315.79
2026-08-27T15:58:54 | 0.23 | 315.79
2026-08-27T15:59:00 | 0.46 | 315.79
2026-08-27T15:59:06 | 0.46 | 315.79
2026-08-27T15:59:11 | 0.46 | 315.79
2026-08-27T15:59:16 | 0.46 | 315.79
2026-08-27T15:59:21 | 0.46 | 315.79
2026-08-27T15:59:26 | 0.46 | 315.79
2026-08-27T15:59:32 | 0.3 | 315.79
2026-08-27T15:59:37 |  | 315.79
2026-08-27T15:59:42 |  | 315.79
2026-08-27T15:59:47 |  | 315.79
2026-08-27T15:59:52 |  | 315.79
2026-08-27T15:59:59 | 1.35 | 315.79
2026-08-27T16:00:05 | 0.45 | 315.79
2026-08-27T16:00:10 | 0.45 | 315.79
2026-08-27T16:00:15 | 0.45 | 315.79
2026-08-27T16:00:20 | 0.45 | 315.79
2026-08-27T16:00:25 | 0.45 | 315.79
2026-08-27T16:00:31 | 0.22 | 315.79
2026-08-27T16:00:37 | 0.22 | 315.79
2026-08-27T16:00:42 | 0.45 | 315.79
2026-08-27T16:00:47 | 0.45 | 315.79
2026-08-27T16:00:52 | 0.22 | 315.79
2026-08-27T16:00:57 | 0.22 | 315.79
2026-08-27T16:01:03 | 75.34 | 315.79
2026-08-27T16:01:08 | 75.42 | 315.79
2026-08-27T16:01:13 | 75.42 | 315.79
2026-08-27T16:01:18 | 75.42 | 315.79
2026-08-27T16:01:23 | 75.17 | 315.79
2026-08-27T16:01:28 | 75.17 | 315.79
2026-08-27T16:01:34 | 75.17 | 315.79
2026-08-27T16:01:39 | 75.34 | 315.79
2026-08-27T16:01:44 | 75.17 | 315.79
2026-08-27T16:01:49 | 75.42 | 315.79
2026-08-27T16:01:54 | 75.42 | 315.79
2026-08-27T16:01:59 | 75.42 | 315.79
2026-08-27T16:02:05 | 75.42 | 315.79
2026-08-27T16:02:10 | 75.42 | 315.79
2026-08-27T16:02:15 | 75.42 | 315.79
2026-08-27T16:02:20 | 75.67 | 315.79
2026-08-27T16:02:25 | 75.42 | 315.79
2026-08-27T16:02:30 | 75.42 | 315.79
2026-08-27T16:02:35 | 75.67 | 315.79
2026-08-27T16:02:41 | 75.67 | 315.79
2026-08-27T16:02:46 | 75.59 | 315.79
2026-08-27T16:02:51 | 75.67 | 315.79
2026-08-27T16:02:56 | 75.67 | 315.79
2026-08-27T16:03:01 | 75.42 | 315.79
2026-08-27T16:03:06 | 75.42 | 315.79
2026-08-27T16:03:12 | 75.42 | 315.79
2026-08-27T16:03:17 | 0.44 | 315.79
2026-08-27T16:03:22 | 0.44 | 315.79
2026-08-27T16:03:27 | 0.67 | 68.32
2026-08-27T16:03:32 | 0.45 | 68.04
2026-08-27T16:03:38 | 0.67 | 68.97
2026-08-27T16:03:43 | 0.67 | 69.29
2026-08-27T16:03:49 | 0.89 | 69.36
2026-08-27T16:03:54 | 0.67 | 69.73
2026-08-27T16:03:59 | 0.45 | 69.73
2026-08-27T16:04:04 | 0.44 | 69.95
2026-08-27T16:04:09 | 0.44 | 69.84
2026-08-27T16:04:15
2026-08-27T16:04:29 | 0.23 | 102.08
2026-08-27T16:04:35 | 0 | 102.08
2026-08-27T16:04:40 | 0.23 | 102.08
2026-08-27T16:04:45 | 0.23 | 101.54
2026-08-27T16:04:50 | 0.23 | 101.54
2026-08-27T16:04:55 | 0.46 | 136.48
2026-08-27T16:05:01 | 0.23 | 148.13
2026-08-27T16:05:06 | 0 | 148.13
2026-08-27T16:05:11 | 0.23 | 148.13
2026-08-27T16:05:17 | 0.23 | 148.13
2026-08-27T16:05:23 | 0 | 148.13
2026-08-27T16:05:28 | 0 | 148.13
2026-08-27T16:05:33 | 0 | 148.13
2026-08-27T16:05:38 | 0 | 148.13
2026-08-27T16:05:43 | 0 | 148.13
2026-08-27T16:05:49 | 0.23 | 148
2026-08-27T16:05:54 | 0.23 | 147.87
2026-08-27T16:05:59 | 0 | 148
2026-08-27T16:06:04 | 0.23 | 148
2026-08-27T16:06:09 | 0.23 | 147.87
2026-08-27T16:06:15 | 0.23 | 148
2026-08-27T16:06:20 | 0.23 | 148
2026-08-27T16:06:25 | 0.46 | 147.87
2026-08-27T16:06:30 | 0.46 | 147.87
2026-08-27T16:06:35 | 0.23 | 147.87
2026-08-27T16:06:41 | 0.46 | 147.87
2026-08-27T16:06:47 | 0.46 | 147.87
2026-08-27T17:08:04 | 0.56 | 315.79
2026-08-27T17:08:09 | 0.56 | 315.79
2026-08-27T17:08:14 | 0.56 | 315.79
2026-08-27T17:08:19 | 0.38 | 315.79
2026-08-27T17:08:24 | 0.56 | 315.79
2026-08-27T17:08:31 | 0.45 | 315.79
2026-08-27T17:08:36 | 0.45 | 315.79
2026-08-27T17:08:43 | 0.45 | 315.79
2026-08-27T17:08:49 | 0.45 | 315.79
2026-08-27T17:08:54 | 0.45 | 315.79
2026-08-27T17:08:59 | 0.45 | 315.79
2026-08-27T17:09:04 | 0.45 | 315.79
2026-08-27T17:09:10 | 0.23 | 315.79
2026-08-27T17:09:15 | 0.23 | 315.79
2026-08-27T17:09:20 | 0.23 | 315.79
2026-08-27T17:09:25 | 0 | 315.79
2026-08-27T17:09:32 | 0.23 | 315.79
2026-08-27T17:09:38 | 0.23 | 315.79
2026-08-27T17:09:43 | 0 | 315.79
2026-08-27T17:09:48 | 0 | 315.79
2026-08-27T17:09:53 | 0.23 | 315.79
2026-08-27T17:09:59 | 0.23 | 315.79
2026-08-27T17:10:04 | 0.23 | 307.69
2026-08-27T17:10:09 | 0.23 | 307.69
2026-08-27T17:10:14 | 0.45 | 307.69
2026-08-27T17:10:21 | 0.45 | 307.69
2026-08-27T17:10:26 | 0.45 | 307.69
2026-08-27T17:10:31 | 0.23 | 307.69
2026-08-27T17:10:36 | 0.45 | 307.69
2026-08-27T17:10:43 | 0.23 | 307.69
2026-08-27T17:10:48 | 0.23 | 307.69
2026-08-27T17:10:53 | 0.45 | 307.69
2026-08-27T17:10:58 | 0.45 | 307.3
2026-08-27T17:11:03 | 0.45 | 307.3
2026-08-27T17:11:09 | 0.45 | 303.41
2026-08-27T17:11:15 | 0.45 | 303.41
2026-08-27T17:11:21 | 0.45 | 303.41
2026-08-27T17:11:26 | 0.45 | 298.14
2026-08-27T17:11:32 | 0.68 | 298.14
2026-08-27T17:11:37 | 0.68 | 298.14
2026-08-27T17:11:42 | 0.68 | 298.14
2026-08-27T17:11:48 | 0.45 | 298.14
2026-08-27T17:11:53 | 0.23 | 298.14
2026-08-27T17:11:58 | 0.23 | 298.14
2026-08-27T17:12:04 | 0.23 | 298.14
2026-08-27T17:12:10 | 0.45 | 298.14
2026-08-27T17:12:15 | 0.45 | 298.14
2026-08-27T17:12:20 | 0.68 | 298.14
2026-08-27T17:12:25 | 0.46 | 298.14
2026-08-27T17:12:30 | 0.23 | 298.14
2026-08-27T17:12:36 | 0.45 | 298.14
2026-08-27T17:12:41 | 0.23 | 298.14
2026-08-27T17:12:46 | 0.45 | 298.14
2026-08-27T17:12:51 | 0.45 | 298.14
2026-08-27T17:12:56 | 0.45 | 298.14
2026-08-27T17:13:02 | 0.23 | 298.14
2026-08-27T17:13:07 | 0.45 | 312.43
2026-08-27T17:13:12 | 0.23 | 312.43
2026-08-27T17:13:17 | 0.45 | 312.43
2026-08-27T17:13:23 | 0.45 | 312.43
2026-08-27T17:13:30 | 0.45 | 312.43
2026-08-27T17:13:35 | 0.45 | 477.58
2026-08-27T17:13:40 | 0.45 | 477.58
2026-08-27T17:13:45 | 0.68 | 477.58
2026-08-27T17:13:51 | 0.45 | 477.58
2026-08-27T17:13:56 | 0.45 | 243.56
2026-08-27T17:14:01 | 0.45 | 243.56
2026-08-27T17:14:06 | 0.45 | 243.56
2026-08-27T17:14:11 | 0.23 | 243.56
2026-08-27T17:14:17 | 0 | 243.56
2026-08-27T17:14:22 | 0.46 | 243.56
2026-08-27T17:14:27 | 0.23 | 243.56
2026-08-27T17:14:32 | 0.23 | 255.32
2026-08-27T17:14:37 | 0 | 255.32
2026-08-27T17:14:43 | 0 | 255.32
2026-08-27T17:14:48 | 0.23 | 298.14
2026-08-27T17:14:55 | 0.23 | 301.84
2026-08-27T17:15:00 | 0.46 | 301.84
2026-08-27T17:15:07 | 0.23 | 301.84
2026-08-27T17:15:12 | 0.46 | 301.84
2026-08-27T17:15:18 | 0.46 | 301.84
2026-08-27T17:15:23 | 0.23 | 350.77
2026-08-27T17:15:28 | 0.23 | 350.77
2026-08-27T17:15:33 | 0.23 | 350.77
2026-08-27T17:15:38 | 0.23 | 350.77
2026-08-27T17:15:44 | 0.46 | 350.77
2026-08-27T17:15:50 | 0.23 | 350.77
2026-08-27T17:15:56 | 0.23 | 350.77
2026-08-27T17:16:01 | 0.23 | 350.77
2026-08-27T17:16:06 | 0.46 | 350.77
2026-08-27T17:16:12 | 0.23 | 350.77
2026-08-27T17:16:17 | 0.46 | 350.77
2026-08-27T17:16:22 | 0.46 | 350.77
2026-08-27T17:16:27 | 0.23 | 350.77
2026-08-27T17:16:34 | 0.23 | 350.77
2026-08-27T17:16:39 | 0.23 | 350.77
2026-08-27T17:16:45 | 0.23 | 350.77
2026-08-27T17:16:50 | 0.45 | 350.77
2026-08-27T17:16:55 | 0.23 | 350.77
2026-08-27T17:17:00 | 0.45 | 350.77
2026-08-27T17:17:05 | 0.23 | 350.77
2026-08-27T17:17:11 | 0.45 | 350.77
2026-08-27T17:17:17 | 0 | 350.77
2026-08-27T17:17:22 | 0.46 | 350.77
2026-08-27T17:17:27 | 0.23 | 350.77
2026-08-27T17:17:33 | 0.46 | 350.77
2026-08-27T17:17:38 | 0.23 | 350.77
2026-08-27T17:17:43 | 0.23 | 350.77
2026-08-27T17:17:48 | 0.46 | 350.77
2026-08-27T17:17:53 | 0.23 | 350.77
2026-08-27T17:18:00 | 0.23 | 350.77
2026-08-27T17:18:05 | 0.23 | 350.77
2026-08-27T17:18:10 | 0.46 | 350.77
2026-08-27T17:18:15 | 0.23 | 350.77
2026-08-27T17:18:20 | 0.23 | 350.77
2026-08-27T17:18:26 | 0.46 | 350.77
2026-08-27T17:18:31 | 0.23 | 350.77
2026-08-27T17:18:36 | 0.46 | 350.77
2026-08-27T17:18:42 | 0.46 | 350.77
2026-08-27T17:18:48 | 0.46 | 350.77
2026-08-27T17:18:53 | 0.46 | 350.77
2026-08-27T17:18:59 | 0.68 | 350.77
2026-08-27T17:19:04 | 0.69 | 350.77
2026-08-27T17:19:09 | 0.69 | 350.77
2026-08-27T17:19:15 | 0.69 | 350.77
2026-08-27T17:19:20 | 0.69 | 350.77
2026-08-27T17:19:25 | 0.46 | 350.77
2026-08-27T17:19:30 | 0.68 | 350.77
2026-08-27T17:19:35 | 0.68 | 350.77
2026-08-27T17:19:41 | 0.46 | 350.77
2026-08-27T17:19:46 | 0.68 | 350.77
2026-08-27T17:19:51 | 0.46 | 350.77
2026-08-27T17:19:56 | 0.46 | 350.77
2026-08-27T17:20:01 | 0.46 | 350.77
2026-08-27T17:20:08 | 0.23 | 350.77
2026-08-27T17:20:12 | 0.23 | 350.77
2026-08-27T17:20:17 | 0.46 | 350.77
2026-08-27T17:20:22 | 0.23 | 350.77
2026-08-27T17:20:27 | 0.23 | 350.77
2026-08-27T17:20:33 | 0.23 | 350.77
2026-08-27T17:20:39 | 0.23 | 350.77
2026-08-27T17:20:44 | 0.23 | 350.77
2026-08-27T17:20:50 | 0 | 350.77
2026-08-27T17:20:57 | 0.23 | 350.77
2026-08-27T17:21:02 | 0.23 | 350.77
2026-08-27T17:21:07 | 0.23 | 350.77
2026-08-27T17:21:13 | 0.23 | 350.77
2026-08-27T17:21:20 | 0.46 | 350.77
2026-08-27T17:21:25 | 200
2026-08-27T17:21:42 | 0.46 | 350.77
2026-08-27T17:21:47 | 0.46 | 350.77
2026-08-27T17:21:52 | 0.46 | 350.77
2026-08-27T17:21:58 | 0.46 | 350.77
2026-08-27T17:22:03 | 0.46 | 350.77
2026-08-27T17:22:08 | 0.46 | 350.77
2026-08-27T17:22:14 | 0.68 | 350.77
2026-08-27T17:22:19 | 0.68 | 350.77
2026-08-27T17:22:24 | 0.46 | 350.77
2026-08-27T17:22:29 | 0.46 | 350.77
2026-08-27T17:22:34 | 0.46 | 350.77
2026-08-27T17:22:39 | 0.46 | 350.77
2026-08-27T17:22:45 | 0.46 | 350.77
2026-08-27T17:22:51 | 0.46 | 350.77
2026-08-27T17:22:57 | 0.68 | 350.77
2026-08-27T17:23:02 | 0.91 | 350.77
2026-08-27T17:34:10 | 0.45 | 350.77
2026-08-27T17:34:15 | 0.45 | 350.77
2026-08-27T17:34:22 | 0.45 | 350.77
2026-08-27T17:34:28 | 0.45 | 350.77
2026-08-27T17:34:33 | 0.68 | 350.77
2026-08-27T17:34:38 | 0.45 | 350.77
2026-08-27T17:34:43 | 0.68 | 350.77
2026-08-27T17:34:49 | 0.68 | 350.77
2026-08-27T17:34:54 | 0.45 | 350.77
2026-08-27T17:34:59 | 0.45 | 350.77
2026-08-27T17:35:04 | 0.45 | 350.77
2026-08-27T17:35:09 | 0.23 | 350.77
2026-08-27T17:35:14 | 0.45 | 350.77
2026-08-27T17:35:21 | 0.45 | 350.77
2026-08-27T17:35:29 | 0.68 | 350.77
2026-08-27T17:35:35 | 0.45 | 350.77
2026-08-27T17:35:40 | 0.45 | 350.77
2026-08-27T17:35:45 | 0.45 | 350.77
2026-08-27T17:35:50 | 0.45 | 350.77
2026-08-27T17:35:56 | 0.23 | 350.77
2026-08-27T17:36:01 | 0.23 | 350.77
2026-08-27T17:36:06 | 0.23 | 350.77
2026-08-27T17:36:11 | 0.23 | 350.77
2026-08-27T17:36:16 | 0.45 | 350.77
2026-08-27T17:36:21 | 0.45 | 350.77
2026-08-27T17:36:27 | 0.45 | 350.77
2026-08-27T17:36:33 | 0.45 | 350.77
2026-08-27T17:36:38 | 0.45 | 350.77
2026-08-27T17:36:43 | 0.45 | 350.77
2026-08-27T17:36:48 | 0.45 | 350.77
2026-08-27T17:36:54 | 0.45 | 350.77
2026-08-27T17:36:59 | 0.45 | 350.77
2026-08-27T17:37:05 | 0.45 | 350.77
2026-08-27T17:37:11 | 0.45 | 350.77
2026-08-27T17:37:16 | 0.45 | 350.77
2026-08-27T17:37:21 | 0.45 | 350.77
2026-08-27T17:37:27 | 0.45 | 350.77
2026-08-27T17:37:32 | 0.23 | 350.77
2026-08-27T17:37:38 | 0.23 | 350.77
2026-08-27T17:37:43 | 0 | 350.77

## Fault Event Log
Timestamp | Fault | State
2026-08-25T17:47:40 | dry_run | CLEARED
2026-08-25T17:47:40 | overvoltage | ACTIVE
2026-08-25T17:47:50 | overvoltage | CLEARED
2026-08-25T17:47:55 | undervoltage | ACTIVE
2026-08-25T17:48:11 | undervoltage | CLEARED
2026-08-25T17:48:16 | stall_pump | ACTIVE
2026-08-25T17:48:21 | stall_pump | CLEARED
2026-08-25T17:48:40 | overload | ACTIVE
2026-08-25T17:48:45 | overload | CLEARED
2026-08-25T18:14:23 | dry_run | ACTIVE
2026-08-25T18:19:20 | dry_run | CLEARED
2026-08-25T18:19:41 | dry_run | ACTIVE
2026-08-25T18:20:06 | dry_run | CLEARED
2026-08-25T18:20:26 | dry_run | ACTIVE
2026-08-25T18:20:42 | dry_run | CLEARED
2026-08-25T18:28:06 | undervoltage | ACTIVE
2026-08-25T18:28:52 | undervoltage | CLEARED
2026-08-25T18:30:09 | undervoltage | ACTIVE
2026-08-25T18:30:30 | undervoltage | CLEARED
2026-08-25T18:30:46 | overvoltage | ACTIVE
2026-08-25T18:30:56 | overvoltage | CLEARED
2026-08-25T18:31:11 | overload | ACTIVE
2026-08-25T18:31:16 | overload | CLEARED
2026-08-25T18:33:51 | undervoltage | ACTIVE
2026-08-26T16:43:32 | dry_run | ACTIVE
2026-08-26T16:43:37 | dry_run | CLEARED
2026-08-26T16:44:07 | dry_run | ACTIVE
2026-08-26T16:44:12 | dry_run | CLEARED
2026-08-26T16:44:42 | dry_run | ACTIVE
2026-08-26T16:44:47 | dry_run | CLEARED
2026-08-26T16:45:17 | dry_run | ACTIVE
2026-08-26T16:45:22 | dry_run | CLEARED
2026-08-26T16:46:28 | dry_run | ACTIVE
2026-08-26T16:46:33 | dry_run | CLEARED
2026-08-26T16:47:08 | dry_run | ACTIVE
2026-08-26T16:47:13 | dry_run | CLEARED
2026-08-26T16:47:23 | dry_run | ACTIVE
2026-08-26T16:47:34 | dry_run | CLEARED
2026-08-26T16:47:49 | dry_run | ACTIVE
2026-08-26T16:47:59 | dry_run | CLEARED
2026-08-26T16:49:54 | dry_run | ACTIVE
2026-08-26T16:49:59 | dry_run | CLEARED
2026-08-26T16:50:09 | dry_run | ACTIVE
2026-08-26T16:50:14 | dry_run | CLEARED
2026-08-26T16:50:24 | dry_run | ACTIVE
2026-08-26T16:50:29 | dry_run | CLEARED
2026-08-26T16:50:54 | dry_run | ACTIVE
2026-08-26T16:50:59 | dry_run | CLEARED
2026-08-26T16:51:09 | dry_run | ACTIVE
2026-08-26T16:51:14 | dry_run | CLEARED
2026-08-26T17:02:37 | undervoltage | CLEARED
2026-08-27T12:20:31 | undervoltage | CLEARED
2026-08-27T12:23:04 | dry_run | ACTIVE
2026-08-27T12:27:20 | dry_run | CLEARED
2026-08-27T12:43:19 | overload | ACTIVE
2026-08-27T12:43:24 | overload | CLEARED
2026-08-27T12:44:15 | overvoltage | ACTIVE
2026-08-27T12:53:01 | overvoltage | CLEARED
2026-08-27T13:00:35 | undervoltage | ACTIVE
2026-08-27T13:00:45 | undervoltage | CLEARED
2026-08-27T13:00:45 | overvoltage | ACTIVE
2026-08-27T13:01:01 | overvoltage | CLEARED
2026-08-27T13:01:12 | phase_loss | ACTIVE
2026-08-27T13:01:23 | undervoltage | ACTIVE
2026-08-27T13:01:23 | phase_loss | CLEARED
2026-08-27T13:01:28 | undervoltage | CLEARED
2026-08-27T15:26:10 | undervoltage | CLEARED
2026-08-27T15:27:16 | undervoltage | ACTIVE
2026-08-27T15:29:17 | undervoltage | CLEARED
2026-08-27T15:31:31 | undervoltage | ACTIVE
2026-08-27T15:32:48 | undervoltage | CLEARED
2026-08-27T15:38:08 | undervoltage | ACTIVE
2026-08-27T15:38:23 | undervoltage | CLEARED
2026-08-27T15:47:57 | undervoltage | CLEARED
2026-08-27T15:59:37 | undervoltage | ACTIVE
2026-08-27T15:59:59 | undervoltage | CLEARED
2026-08-27T16:01:03 | phase_loss | ACTIVE
2026-08-27T16:03:17 | phase_loss | CLEARED
2026-08-27T16:03:43 | stall_pump | ACTIVE
2026-08-27T16:03:49 | stall_pump | CLEARED
2026-08-27T17:08:31 | overvoltage | CLEARED
2026-08-27T17:08:54 | dry_run | ACTIVE
2026-08-27T17:09:10 | dry_run | CLEARED
2026-08-27T17:21:52 | dry_run | ACTIVE
2026-08-27T17:37:21 | dry_run | CLEARED
2026-08-27T17:37:38 | dry_run | ACTIVE